## LowH2O DBH
Selectiontool LowH2O Hybrids
|  |  |  | Taal/Language/Sprache/Språk/Jazyk |  |  |  | English
|  |  |  | Hybrid device |  |  |  | Strada Hybrid
|  |  |  | Version [centimeter] |  |  |  | 26dB(A) | 50 | 21 | 21.5
[5 empty] | Length | Fan speed |  |  | Heigth | Type | Depth
Temperatures
Heating: |  |  |  |  | Cooling:
Supply water | 0 | 0 | 75 | °C | Supply water | 0 | 0 | 16 | °C | Unit conversion
Return water | 0 | 0 | 65 | °C | Return water | 0 | 0 | 18 | °C
Entering air (dry bulb) | 0 | 0 | 20 | °C | Entering air (dry bulb) | 0 | 0 | 27 | °C
[5 empty] | rel. humid. |  |  | 50%
Length [cm] |  | Heating capacity [W] | Water flow [kg/h] | Water side pressure loss [kPa] | Cooling capacity [W]** | Water flow [kg/h] | Water side pressure loss [kPa] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]**** | Electrical consumption [W] | Water volume [l]
Strada Hybrid, Heigth 50cm, Type 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
60 |  | 1803 | 155 | 0.13454 | 234 | 101 | 0.057851 | 26 | 34 | 4.8 | 1.6
70 |  | 1978 | 170 | 0.1649 | 240 | 103 | 0.061591 | 26 | 34 | 5.1 | 1.9
80 |  | 2628 | 226 | 0.2945 | 341 | 147 | 0.12659 | 26 | 34 | 6 | 2.1
90 |  | 3009 | 259 | 0.39212 | 390 | 168 | 0.1679 | 26 | 34 | 7 | 2.4
100 |  | 3388 | 291 | 0.50157 | 439 | 189 | 0.2156 | 26 | 34 | 7 | 2.7
110 |  | 3556 | 306 | 0.563 | 446 | 192 | 0.22662 | 26 | 34 | 7.9 | 2.9
120 |  | 4175 | 359 | 0.78201 | 542 | 233 | 0.33654 | 26 | 34 | 8.7 | 3.2
140 |  | 4951 | 426 | 1.1262 | 642 | 276 | 0.48412 | 26 | 34 | 9.6 | 3.7
160 |  | 5690 | 489 | 1.5162 | 738 | 317 | 0.65391 | 26 | 34 | 11.5 | 4.3
180 |  | 6017 | 517 | 1.7365 | 750 | 323 | 0.69903 | 26 | 34 | 11.5 | 4.8
200 |  | 7299 | 628 | 2.5976 | 947 | 407 | 1.1239 | 26 | 34 | 13.2 | 5.3
220 |  | 8103 | 697 | 3.257 | 1051 | 452 | 1.4133 | 26 | 34 | 15.5 | 5.9
240 |  | 8907 | 766 | 4.0011 | 1155 | 497 | 1.7405 | 26 | 34 | 16.4 | 6.4
260 |  | 9235 | 794 | 4.3863 | 1168 | 502 | 1.8191 | 26 | 34 | 16.4 | 6.9
280 |  | 10516 | 904 | 5.7534 | 1364 | 587 | 2.5138 | 26 | 34 | 19.3 | 7.5
300 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
v2023-05-24
* | If the fans are switched off, the output is an indicative value.
** | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
*** | When the water volume is given in gallons, the units are specifically imperial gallons.
**** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).
SI-units
Imperial-units
Copy all data

## data (hidden)
Strada_L | [11 empty] | heating | Ti | 75 | 75 | [20 empty] | cooling | Ti | 16 | 16 |  | RH | 50% |  |  |  | RH | [24 empty] | DBH rail | NONE | 10 | 15 |  |  | Imperial/SI |  | toestel | taal | lengte | hoogte | type | Built_in Hybrid |  |  | Strada Hybrid |  |  | Linea Hybrid |  |  | Tempo Hybrid |  |  | DBH-upgrade |  |  | Mini Hybrid |  |  | Strada hybrid MM
Strada | [12 empty] | Tr | 65 | 65 | [21 empty] | Tr | 18 | 18 | [31 empty] | 1 | [5 empty] | 1 |  | Geselecteerd |  |  |  |  | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | hoogte | lengte | type | Selectiontool LowH2O Hybrids
Strada_T | [12 empty] | Ta | 20 | 20 | [21 empty] | Ta | 27 | 27 | [37 empty] | 1 | Strada | Strada Hybrid | Nederlands | 50 | 35 | 10 | 20 | 50 | 10 | 35 | 50 | 10 | 20 | 50 | 10 | 20 | 50 | 10 |  | 50 | 10 | 28 | N.v.t. | 11 | 35 | 60 | 11
kolomindex | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 |  | Linea | Linea Hybrid | English | 60 | 50 | 11 | 30 | 60 | 11 | 50 | 60 | 11 | 35 | 60 | 11 | 30 | 60 | 11 |  | 60 | 11 |  | 81 | 16 | 50 | 80 | 16 |  |  |  |  | Taal/Language/Sprache/Langue/Språk/Lengua |  |  |  | English | 0
1505021 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | Tempo | Tempo Hybrid | Français | 70 | 65 | 15 | 40 | 70 | 15 | 65 | 70 | 15 | 50 | 70 | 15 | 40 | 70 | 15 |  | 70 | 15 |  | 101 |  | 65 | 100 | 21 |  |  |  |  | 0 |  |  |  | Strada Hybrid | 0
1506021 |  |  | 1 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1239 | 1803 | 1935 | 2561 | 107 | 155 | 166 | 220 | 0.064814 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 | 0 | 1549 | 0 | 0.8 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 234 | 251 | 332 | 0 | 0 | 0 | 0 | 1 |  | Built_in | Built_in Hybrid | Deutsch | 80 | 95 | 16 | 50 | 80 | 16 | 95 | 80 | 16 | 65 | 80 | 16 | 50 | 80 | 16 |  | 80 | 16 |  | 121 |  |  | 120 | [5 empty] | [centimeter] |  |  |  | 26dB(A) | 50 | 21 | 0
1507021 |  |  | 1 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1446 | 1978 | 2123 | 2810 | 124 | 170 | 183 | 242 | 0.088673 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 | 0 | 1807 | 0 | 0.8 | 0 | 0 | 0 | 12.3 | 14.4 | 21.85 | 0 | 1 | 1 | 1 | 240 | 258 | 341 | 0 | 0 | 0 | 0 | 1 |  | MiniHybrid | Mini Hybrid | Norsk | 90 | 0 | 20 | 60 | 90 | 20 |  | 90 | 20 | 95 | 90 | 20 | 60 | 90 | 20 |  | 90 | 20 |  | 141 |  |  | 140 | [6 empty] | 0 |  | 0 |  | 0 | 0 | 0
1508021 |  |  | 1 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1653 | 2628 | 2818 | 3781 | 142 | 226 | 242 | 325 | 0.11828 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 | 0 | 2066 | 0 | 0.8 | 0 | 0 | 0 | 11.8 | 13.7 | 21.85 | 0 | 1 | 1 | 1 | 341 | 366 | 490 | 0 | 0 | 0 | 0 | 1 |  | StradaMM | Strada Hybrid MM | Español | 100 | 0 | 21 | 70 | 100 | 21 |  | 100 | 21 |  | 100 | 21 | 70 | 100 | 21 |  | 100 | 21 |  | 181 |  |  |  |  | 0
1509021 |  |  | 1 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1859 | 3009 | 3224 | 4391 | 160 | 259 | 277 | 378 | 0.1526 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 | 0 | 2324 | 0 | 0.8 | 0 | 0 | 0 | 11.3 | 13.2 | 21.85 | 0 | 1 | 1 | 1 | 390 | 418 | 570 | 0 | 0 | 0 | 0 | 1 |  | #REF! | 1 | Svenska | 110 | 0 |  | 90 | 110 |  |  | 110 |  |  | 110 |  | 90 | 110 |  |  | 110 |  |  | 241 |  |  |  |  | 0 |  |  |  |  | 0
15010021 |  |  | 1 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2066 | 3388 | 3627 | 5000 | 178 | 291 | 312 | 430 | 0.19177 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 | 0 | 2582 | 0 | 0.8 | 0 | 0 | 0 | 10.9 | 12.8 | 21.85 | 0 | 1 | 1 | 1 | 439 | 471 | 649 | 0 | 0 | 0 | 0 | 1 |  | W/m,beript dyn heat | W/m,beript dyn cool | Čeština | 120 | 0 |  |  | 120 |  |  | 120 |  |  | 120 |  |  | 120 |  |  | 120 | [7 empty] | 0 | 0 | 0 | 75 | °C | 0 | 0 | 0 | 16 | °C | 0
15011021 |  |  | 1 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2272 | 3556 | 3808 | 5249 | 195 | 306 | 327 | 451 | 0.23357 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 | 0 | 2840 | 0 | 0.8 | 0 | 0 | 0 | 10.9 | 12.8 | 21.85 | 0 | 1 | 1 | 1 | 446 | 477 | 658 | 0 | 0 | 0 | 0 | 1 |  |  | 1 | ExtraTaal1 | 140 | 0 |  |  | 140 |  |  | 140 |  |  | 140 |  |  | 140 |  |  | 140 | [7 empty] | 0 | 0 | 0 | 65 | °C | 0 | 0 | 0 | 18 | °C
15012021 |  |  | 1 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2478 | 4175 | 4471 | 6220 | 213 | 359 | 385 | 535 | 0.28258 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 | 0 | 3098 | 0 | 0.8 | 0 | 0 | 0 | 10.6 | 12.5 | 21.85 | 0 | 1 | 1 | 1 | 542 | 580 | 807 | 0 | 0 | 0 | 0 | 1 |  | OFF |  | ExtraTaal2 | 160 | 0 |  |  | 160 |  |  | 160 |  |  | 160 |  |  | 160 |  |  | 160 | [7 empty] | 0 | 0 | 0 | 20 | °C | 0 | 0 | 0 | 27 | °C
15014021 |  |  | 1 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2892 | 4951 | 5302 | 7440 | 249 | 426 | 456 | 640 | 0.39641 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 | 0 | 3615 | 0 | 0.8 | 0 | 0 | 0 | 10.4 | 12.2 | 21.85 | 0 | 1 | 1 | 1 | 642 | 688 | 965 | 0 | 0 | 0 | 0 | 1 |  | 26dB(A) |  | ExtraTaal3 | 180 | 0 | Copy all data |  | 180 |  |  | 180 |  |  | 180 |  |  | 180 |  |  | 180 | [12 empty] | 0 |  |  | 50%
15016021 |  |  | 1 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3305 | 5690 | 6075 | 8659 | 284 | 489 | 522 | 745 | 0.52853 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 | 0 | 4131 | 0 | 0.8 | 0 | 0 | 0 | 10 | 11.8 | 21.85 | 0 | 1 | 1 | 1 | 738 | 788 | 1123 | 0 | 0 | 0 | 0 | 1 |  | 30dB(A) |  |  | 200 | 0 | SI-units |  | 200 |  |  | 200 |  |  | 200 |  |  | 200 |  |  | 200
15018021 |  |  | 1 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3718 | 6017 | 6424 | 9157 | 320 | 517 | 552 | 788 | 0.68655 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 | 0 | 4648 | 0 | 0.8 | 0 | 0 | 0 | 10 | 11.8 | 21.85 | 0 | 1 | 1 | 1 | 750 | 801 | 1142 | 0 | 0 | 0 | 0 | 1 |  | MAX |  |  | 220 | 0 | Imperial-units |  | 220 |  |  | 220 |  |  | 220 |  |  | 220 |  |  | 220
15020021 |  |  | 1 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4131 | 7299 | 7690 | 11098 | 355 | 628 | 661 | 954 | 0.8636 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 | 0 | 5164 | 0 | 0.8 | 0 | 0 | 0 | 10 | 11.4 | 21.85 | 0 | 1 | 1 | 1 | 947 | 998 | 1440 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | 240 | 0 |  |  | 240 |  |  | 240 |  |  | 240 |  |  | 240 |  |  | 240 | [7 empty] | [cm] | 0 |  |  | [ONWAAR] |  |  | [ONWAAR] | 0 | 0 | 0
15022021 |  |  | 1 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4239.1072 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4239 | 8103 | 8440 | 12318 | 365 | 697 | 726 | 1059 | 0.93691 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 | 0 | 5298.8841 | 0 | 0.8 | 0 | 0 | 0 | 10 | 11.1 | 21.85 | 0 | 1 | 1 | 1 | 1051 | 1095 | 1598 | 0 | 0 | 0 | 0 | 1 |  |  |  | 2 | 260 | 0 |  |  | 260 |  |  | 260 |  |  | 260 |  |  | 260 |  |  | 260 | [7 empty] | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15024021 |  |  | 1 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4958 | 8907 | 9231 | 13538 | 426 | 766 | 794 | 1164 | 1.2947 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 | 0 | 6197 | 0 | 0.8 | 0 | 0 | 0 | 10 | 10.9 | 21.85 | 0 | 1 | 1 | 1 | 1155 | 1197 | 1756 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | 280 | 0 |  |  | 280 |  |  | 280 |  |  | 280 |  |  | 280 |  |  | 280 | [7 empty] | 50 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
15026021 |  |  | 1 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5134.1124 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5134 | 9235 | 9571 | 14035 | 442 | 794 | 823 | 1207 | 1.4256 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 | 0 | 6417.6404 | 0 | 0.8 | 0 | 0 | 0 | 10 | 10.9 | 21.85 | 0 | 1 | 1 | 1 | 1168 | 1210 | 1774 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | 0 | 0 |  |  | 300 | [8 empty] | 300 |  |  | 300 | [7 empty] | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
15028021 |  |  | 1 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5784 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 5784 | 10516 | 10751 | 15977 | 497 | 904 | 925 | 1374 | 1.8285 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1364.0875 | 1394.6194 | 2072.42 | 0.85 | 0.85 | 0.85 | 1364 | 1395 | 2072 | 587 | 600 | 891 | 2.5138 | 2.6215 | 5.5955 | 7.5 | 19.3 | 20.4 | 34.5 | 0 | 7230 | 0 | 0.8 | 0 | 0 | 0 | 10 | 10.6 | 21.85 | 0 | 1 | 1 | 1 | 1364 | 1395 | 2072 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | 0 | 0 | [7 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [6 empty] | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
150021 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [6 empty] | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[82 empty] | 0 | [8 empty] | Raillengte | Railtype | BMS-stuurspanningen |  |  | Opgenomen elektrisch vermogen | [8 empty] | 60 | 0 | 1239 | 107 | 0.064814 |  |  |  | 0 | 0 | 0 | 1.6
[90 empty] | 5010 | 50 | 10 | 14.2 | 16.2 | 21.85 | 3.6 | 4.1 | 5.1 | [6 empty] | 60 | 12.3 | 1803 | 155 | 0.13454 | 234 | 101 | 0.057851 | 26 | 34 | 4.8 | 1.6
[90 empty] | 5015 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 60 | 14.4 | 1935 | 166 | 0.15403 | 251 | 108 | 0.066012 | 30 | 38 | 5.5 | 1.6
[90 empty] | 6010 | 60 | 10 | 13.6 | 15.6 | 21.85 | 4.8 | 5.4 | 6.8 | [6 empty] | 60 | 21.85 | 2561 | 220 | 0.26853 | 332 | 143 | 0.11478 | 41.1 | 49.1 | 7.2 | 1.6
[8 empty] | soundpressure level |  |  |  | power | 75/65/20 |  |  | n |  |  |  | result | power |  |  | result | flow |  |  | static pressure loss | [7 empty] | power | 16/18/27 |  | n |  |  | result | power |  | result | flow |  | static pressure loss |  |  |  | electrical power nominal |  |  |  | oude cataloog |  | Statisch met rail / statisch cataloog |  |  |  |  | BMS-stuurspanning |  |  | Sensible heat factor |  |  | Total cooling capacity |  |  |  | Diff. Total and sensible |  |  | Show or not | [13 empty] | 6015 | 60 | 15 | 12.3 | 14.4 | 21.85 | 4.8 | 5.5 | 7.2 | [6 empty] | 70 | 0 | 1446 | 124 | 0.088673 |  |  |  | 0 | 0 | 0 | 1.9
lookup code | L,rail | T,rail | toestel | height | length | type | depth | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | 0 | 1 | 2 | 3 | k1 | n | t | k2 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | 1 | 2 | 3 | watervolume | 1 | 2 | 3 |  | Static,H | Static,C |  |  |  | 0 | 1 | 2 | 3 |  | SHF 1 | SHF 2 | SHF 3 | Q,t 1 | Q,t 2 | Q,t 3 |  | ΔQ,t,s 1 | ΔQ,t,s 2 | ΔQ,t,s 3 | OK/NOTOK | [13 empty] | 7010 | 70 | 10 | 13.2 | 15.1 | 21.85 | 5.5 | 5.9 | 7.9 | [6 empty] | 70 | 12.3 | 1978 | 170 | 0.1649 | 240 | 103 | 0.061591 | 26 | 34 | 5.1 | 1.9
1355010 |  |  | 1 | 35 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 404.1 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 404 | 649 | 695 | 812 | 35 | 56 | 60 | 70 | 0.0057305 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 449 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1 | [13 empty] | 7015 | 70 | 15 | 12.3 | 14.4 | 21.85 | 5.1 | 5.6 | 7.2 | [6 empty] | 70 | 14.4 | 2123 | 183 | 0.19063 | 258 | 111 | 0.071336 | 30 | 38 | 5.6 | 1.9
1505010 |  |  | 1 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 484.2 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 484 | 649 | 695 | 812 | 42 | 56 | 60 | 70 | 0.0081621 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 538 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1 | [13 empty] | 8010 | 80 | 10 | 12.8 | 14.7 | 21.85 | 6.3 | 6.8 | 9.1 | [6 empty] | 70 | 21.85 | 2810 | 242 | 0.33051 | 341 | 147 | 0.12389 | 41.1 | 49.1 | 7.2 | 1.9
1655010 |  |  | 1 | 65 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 545.4 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 545 | 649 | 695 | 812 | 47 | 56 | 60 | 70 | 0.010154 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 606 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1 | [13 empty] | 8015 | 80 | 15 | 11.8 | 13.7 | 21.85 | 6 | 6.7 | 9 | [6 empty] | 80 | 0 | 1653 | 142 | 0.11828 |  |  |  | 0 | 0 | 0 | 2.1
1355011 |  |  | 1 | 35 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 406.64 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 407 | 881 | 943 | 1102 | 35 | 76 | 81 | 95 | 0.0095353 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 598 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1 | [13 empty] | 9010 | 90 | 10 | 12.5 | 14.7 | 21.85 | 6.7 | 7.4 | 10.3 | [6 empty] | 80 | 11.8 | 2628 | 226 | 0.2945 | 341 | 147 | 0.12659 | 26 | 34 | 6 | 2.1
1505011 |  |  | 1 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 471.24 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 471 | 881 | 943 | 1102 | 41 | 76 | 81 | 95 | 0.012936 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 693 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1 | [13 empty] | 9015 | 90 | 15 | 11.3 | 13.2 | 21.85 | 7 | 7.7 | 10.7 | [6 empty] | 80 | 13.7 | 2818 | 242 | 0.33687 | 366 | 157 | 0.14403 | 30 | 38 | 6.7 | 2.1
1655011 |  |  | 1 | 65 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 524.96 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 525 | 881 | 943 | 1102 | 45 | 76 | 81 | 95 | 0.015481 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 136.4943 | 146.0591 | 170.792 | 0.95 | 0.95 | 0.95 | 136 | 146 | 171 | 58 | 63 | 74 | 0.025275 | 0.029658 | 0.040497 | 0.7 | 3.6 | 4.1 | 5.1 |  | 772 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 136 | 146 | 171 |  | 0 | 0 | 0 | 1 | [13 empty] | 10010 | 100 | 10 | 12.3 | 14.1 | 21.85 | 7.8 | 8.7 | 12.2 | [6 empty] | 80 | 21.85 | 3781 | 325 | 0.60165 | 490 | 211 | 0.25733 | 42.4 | 50.4 | 9 | 2.1
1356010 |  |  | 1 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 485.1 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 485 | 842 | 901 | 1066 | 42 | 72 | 77 | 92 | 0.0086709 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 539 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1 | [13 empty] | 10015 | 100 | 15 | 10.9 | 12.8 | 21.85 | 7 | 7.7 | 10.7 | [6 empty] | 90 | 0 | 1859 | 160 | 0.1526 |  |  |  | 0 | 0 | 0 | 2.4
1506010 |  |  | 1 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 581.4 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 581 | 842 | 901 | 1066 | 50 | 72 | 77 | 92 | 0.01214 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 646 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1 | [13 empty] | 11010 | 110 | 10 | 12 | 13.9 | 21.85 | 8.4 | 9.3 | 14 | [6 empty] | 90 | 11.3 | 3009 | 259 | 0.39212 | 390 | 168 | 0.1679 | 26 | 34 | 7 | 2.4
1656010 |  |  | 1 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 654.3 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 654 | 842 | 901 | 1066 | 56 | 72 | 77 | 92 | 0.015112 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 727 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1 | [13 empty] | 11015 | 110 | 15 | 10.9 | 12.8 | 21.85 | 7.9 | 8.8 | 12.5 | [6 empty] | 90 | 13.2 | 3224 | 277 | 0.44738 | 418 | 180 | 0.19218 | 30 | 38 | 7.7 | 2.4
1956010 |  |  | 1 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 746.6923 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 747 | 842 | 901 | 1066 | 64 | 72 | 77 | 92 | 0.019564 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 836 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1 | [13 empty] | 12010 | 120 | 10 | 11.8 | 13.7 | 21.85 | 8.9 | 9.9 | 14.8 | [6 empty] | 90 | 21.85 | 4391 | 378 | 0.82373 | 570 | 245 | 0.35163 | 43.3 | 51.3 | 10.7 | 2.4
1356011 |  |  | 1 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 488.24 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 488 | 1142 | 1223 | 1447 | 42 | 98 | 105 | 124 | 0.014569 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 718 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1 | [13 empty] | 12015 | 120 | 15 | 10.6 | 12.5 | 21.85 | 8.7 | 9.8 | 14.3 | [6 empty] | 100 | 0 | 2066 | 178 | 0.19177 |  |  |  | 0 | 0 | 0 | 2.7
1506011 |  |  | 1 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 565.76 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 566 | 1142 | 1223 | 1447 | 49 | 98 | 105 | 124 | 0.019577 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 832 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1 | [13 empty] | 14010 | 140 | 10 | 11.5 | 13.3 | 21.85 | 10.1 | 11.2 | 17.5 | [6 empty] | 100 | 10.9 | 3388 | 291 | 0.50157 | 439 | 189 | 0.2156 | 26 | 34 | 7 | 2.7
1656011 |  |  | 1 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 629.68 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 630 | 1142 | 1223 | 1447 | 54 | 98 | 105 | 124 | 0.023588 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 176.675 | 189.625 | 223.85 | 0.95 | 0.95 | 0.95 | 177 | 190 | 224 | 76 | 82 | 96 | 0.045491 | 0.052655 | 0.071338 | 0.8 | 4.8 | 5.4 | 6.8 |  | 926 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 177 | 190 | 224 |  | 0 | 0 | 0 | 1 | [13 empty] | 14015 | 140 | 15 | 10.4 | 12.2 | 21.85 | 9.6 | 10.5 | 16.1 | [6 empty] | 100 | 12.8 | 3627 | 312 | 0.57492 | 471 | 203 | 0.24792 | 30 | 38 | 7.7 | 2.7
1956011 |  |  | 1 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 733.04 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 733 | 1142 | 1223 | 1447 | 63 | 98 | 105 | 124 | 0.031715 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 148.025 | 158.875 | 187.55 | 0.95 | 0.95 | 0.95 | 148 | 159 | 188 | 64 | 68 | 81 | 0.032689 | 0.036729 | 0.051426 | 0.8 | 4.8 | 5.4 | 6.8 |  | 1078 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 148 | 159 | 188 |  | 0 | 0 | 0 | 1 | [13 empty] | 16010 | 160 | 10 | 11.2 | 13 | 21.85 | 11 | 12.4 | 19.2 | [6 empty] | 100 | 21.85 | 5000 | 430 | 1.0784 | 649 | 279 | 0.46187 | 44.1 | 52.1 | 10.7 | 2.7
1356015 |  |  | 1 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 705.6 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 706 | 957 | 1028 | 1360 | 61 | 82 | 88 | 117 | 0.019068 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 882 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1 | [13 empty] | 16015 | 160 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6 | [6 empty] | 110 | 0 | 2272 | 195 | 0.23357 |  |  |  | 0 | 0 | 0 | 2.9
1506015 |  |  | 1 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 832 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 832 | 957 | 1028 | 1360 | 72 | 82 | 88 | 117 | 0.026427 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1040 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1 | [13 empty] | 18010 | 180 | 10 | 10.9 | 12.7 | 21.85 | 12.2 | 13.7 | 22 | [6 empty] | 110 | 10.9 | 3556 | 306 | 0.563 | 446 | 192 | 0.22662 | 26 | 34 | 7.9 | 2.9
1656015 |  |  | 1 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1153 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1 | [13 empty] | 18015 | 180 | 15 | 10 | 11.8 | 21.85 | 11.5 | 12.8 | 19.6 | [6 empty] | 110 | 12.8 | 3808 | 327 | 0.64102 | 477 | 205 | 0.2575 | 30 | 38 | 8.8 | 2.9
1956015 |  |  | 1 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1288 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1 | [13 empty] | 20010 | 200 | 10 | 10.7 | 12.5 | 21.85 | 13.4 | 14.8 | 24 | [6 empty] | 110 | 21.85 | 5249 | 451 | 1.2027 | 658 | 283 | 0.48326 | 44.1 | 52.1 | 12.5 | 2.9
1356016 |  |  | 1 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 650.08 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 650 | 1400 | 1503 | 1989 | 56 | 120 | 129 | 171 | 0.046649 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 956 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1 | [13 empty] | 20015 | 200 | 15 | 10 | 11.4 | 21.85 | 13.2 | 14.7 | 23.5 | [6 empty] | 120 | 0 | 2478 | 213 | 0.28258 |  |  |  | 0 | 0 | 0 | 3.2
1506016 |  |  | 1 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 774.52 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 775 | 1400 | 1503 | 1989 | 67 | 120 | 129 | 171 | 0.066509 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1139 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1 | [13 empty] | 22010 | 220 | 10 | 10.5 | 12.3 | 21.85 | 13.4 | 14.8 | 24 | [6 empty] | 120 | 10.6 | 4175 | 359 | 0.78201 | 542 | 233 | 0.33654 | 26 | 34 | 8.7 | 3.2
1656016 |  |  | 1 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 886.72 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 887 | 1400 | 1503 | 1989 | 76 | 120 | 129 | 171 | 0.085347 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 197.95 | 212.75 | 282.125 | 0.95 | 0.95 | 0.95 | 198 | 213 | 282 | 85 | 92 | 121 | 0.10651 | 0.12458 | 0.21435 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1304 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 198 | 213 | 282 |  | 0 | 0 | 0 | 1 | [13 empty] | 22015 | 220 | 15 | 10 | 11.1 | 21.85 | 15.5 | 16.8 | 27.5 | [6 empty] | 120 | 12.5 | 4471 | 385 | 0.89645 | 580 | 249 | 0.38304 | 30 | 38 | 9.8 | 3.2
1956016 |  |  | 1 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1092.08 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1092 | 1400 | 1503 | 1989 | 94 | 120 | 129 | 171 | 0.12999 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 165.85 | 178.25 | 236.375 | 0.95 | 0.95 | 0.95 | 166 | 178 | 236 | 71 | 77 | 101 | 0.074594 | 0.087584 | 0.14986 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1606 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 236 |  | 0 | 0 | 0 | 1 | [13 empty] | 24010 | 240 | 10 | 10.4 | 12.2 | 21.85 | 14.8 | 16.6 | 28 | [6 empty] | 120 | 21.85 | 6220 | 535 | 1.7058 | 807 | 347 | 0.73179 | 44.8 | 52.8 | 14.3 | 3.2
1356020 |  |  | 1 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 988.8 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 989 | 1347 | 1442 | 1706 | 85 | 116 | 124 | 147 | 0.029061 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1236 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1 | [13 empty] | 24015 | 240 | 15 | 10 | 10.9 | 21.85 | 16.4 | 17.7 | 29.7 | [6 empty] | 140 | 0 | 2892 | 249 | 0.39641 |  |  |  | 0 | 0 | 0 | 3.7
1506020 |  |  | 1 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1164 | 1347 | 1442 | 1706 | 100 | 116 | 124 | 147 | 0.040077 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1455 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1 | [13 empty] | 26010 | 260 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 | [6 empty] | 140 | 10.4 | 4951 | 426 | 1.1262 | 642 | 276 | 0.48412 | 26 | 34 | 9.6 | 3.7
1656020 |  |  | 1 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1611 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1 | [13 empty] | 26015 | 260 | 15 | 10 | 10.9 | 21.85 | 16.2 | 18.6 | 31.4 | [6 empty] | 140 | 12.2 | 5302 | 456 | 1.2858 | 688 | 296 | 0.55461 | 30 | 38 | 10.5 | 3.7
1956020 |  |  | 1 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1795 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1 | [13 empty] | 28010 | 280 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 | [6 empty] | 140 | 21.85 | 7440 | 640 | 2.4907 | 965 | 415 | 1.0702 | 45.4 | 53.4 | 16.1 | 3.7
1356021 |  |  | 1 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1014.4 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1014 | 1803 | 1935 | 2561 | 87 | 155 | 166 | 220 | 0.043128 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1268 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1 | [13 empty] | 28015 | 280 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5 | [6 empty] | 160 | 0 | 3305 | 284 | 0.52853 |  |  |  | 0 | 0 | 0 | 4.3
1506021 |  |  | 1 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1239 | 1803 | 1935 | 2561 | 107 | 155 | 166 | 220 | 0.064814 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1549 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1 | [13 empty] | 30010 | 300 | 10 | 10.2 | 11.9 | 21.85 | 16.2 | 18.6 | 31.4 | [6 empty] | 160 | 10 | 5690 | 489 | 1.5162 | 738 | 317 | 0.65391 | 26 | 34 | 11.5 | 4.3
1656021 |  |  | 1 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1454.4 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1454 | 1803 | 1935 | 2561 | 125 | 155 | 166 | 220 | 0.088043 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 216.2921 | 232.1848 | 307.3035 | 0.85 | 0.85 | 0.85 | 216 | 232 | 307 | 93 | 100 | 132 | 0.049177 | 0.056729 | 0.098024 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1818 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 216 | 232 | 307 |  | 0 | 0 | 0 | 1 | [13 empty] | 30015 | 300 | 15 | 10 | 10.6 | 21.85 | 19.3 | 20.4 | 34.5 | [6 empty] | 160 | 11.8 | 6075 | 522 | 1.7213 | 788 | 339 | 0.7447 | 30 | 38 | 12.8 | 4.3
1956021 |  |  | 1 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1707.6437 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1708 | 1803 | 1935 | 2561 | 147 | 155 | 166 | 220 | 0.12119 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 181.2177 | 194.5332 | 257.4705 | 0.85 | 0.85 | 0.85 | 181 | 195 | 257 | 78 | 84 | 111 | 0.03479 | 0.04025 | 0.069672 | 1.6 | 4.8 | 5.5 | 7.2 |  | 2352 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 181 | 195 | 257 |  | 0 | 0 | 0 | 1 | [28 empty] | 160 | 21.85 | 8659 | 745 | 3.4394 | 1123 | 483 | 1.4802 | 46.4 | 54.4 | 19.6 | 4.3
1357010 |  |  | 1 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 566.1 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 566 | 1030 | 1104 | 1320 | 49 | 89 | 95 | 114 | 0.01234 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 629 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1 | [28 empty] | 180 | 0 | 3718 | 320 | 0.68655 |  |  |  | 0 | 0 | 0 | 4.8
1507010 |  |  | 1 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 677.7 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 678 | 1030 | 1104 | 1320 | 58 | 89 | 95 | 114 | 0.017063 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 753 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1 | [28 empty] | 180 | 10 | 6017 | 517 | 1.7365 | 750 | 323 | 0.69903 | 26 | 34 | 11.5 | 4.8
1657010 |  |  | 1 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 763.2 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 763 | 1030 | 1104 | 1320 | 66 | 89 | 95 | 114 | 0.021879 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 848 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1 | [13 empty] | L,rail/L,tot | T10 | T11 | T15 | T16 | T20 | T21 | ALS | [7 empty] | 180 | 11.8 | 6424 | 552 | 1.9715 | 801 | 344 | 0.78947 | 30 | 38 | 12.8 | 4.8
1957010 |  |  | 1 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 877.5 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 878 | 1030 | 1104 | 1320 | 76 | 89 | 95 | 114 | 0.028709 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 975 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 90% | 68% | 80% | 68% | 80% | 80% | #REF! | T10 | [6 empty] | 180 | 21.85 | 9157 | 788 | 3.9339 | 1142 | 491 | 1.5713 | 46.4 | 54.4 | 19.6 | 4.8
1357011 |  |  | 1 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 569.16 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 569 | 1397 | 1498 | 1791 | 49 | 120 | 129 | 154 | 0.020906 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 837 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1 | [13 empty] | 0.8 | 92% | 74.4% | 84% | 74.4% | 84% | 84% | #REF! | T11 | [6 empty] | 200 | 0 | 4131 | 355 | 0.8636 |  |  |  | 0 | 0 | 0 | 5.3
1507011 |  |  | 1 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 659.6 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 660 | 1397 | 1498 | 1791 | 57 | 120 | 129 | 154 | 0.027897 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 970 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1 | [13 empty] | 0.6 | 94% | 80.8% | 88% | 80.8% | 88% | 88% | #REF! | T15 | [6 empty] | 200 | 10 | 7299 | 628 | 2.5976 | 947 | 407 | 1.1239 | 26 | 34 | 13.2 | 5.3
1657011 |  |  | 1 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 734.4 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 734 | 1397 | 1498 | 1791 | 63 | 120 | 129 | 154 | 0.033771 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216.4625 | 232.1327 | 277.537 | 0.95 | 0.95 | 0.95 | 216 | 232 | 278 | 93 | 100 | 120 | 0.071145 | 0.081763 | 0.116 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1080 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 216 | 232 | 278 |  | 0 | 0 | 0 | 1 | [13 empty] | 0.4 | 96% | 87.2% | 92% | 87.2% | 92% | 92% | #REF! | T16 | [6 empty] | 200 | 11.4 | 7690 | 661 | 2.8682 | 998 | 429 | 1.244 | 30 | 38 | 14.7 | 5.3
1957011 |  |  | 1 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 854.76 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 855 | 1397 | 1498 | 1791 | 74 | 120 | 129 | 154 | 0.045934 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.3604 | 194.4896 | 232.531 | 0.95 | 0.95 | 0.95 | 181 | 194 | 233 | 78 | 83 | 100 | 0.050801 | 0.057216 | 0.081763 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1257 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 181 | 194 | 233 |  | 0 | 0 | 0 | 1 | [13 empty] | 0.2 | 98% | 93.6% | 96% | 93.6% | 96% | 96% | #REF! | T20 | [6 empty] | 200 | 21.85 | 11098 | 954 | 5.8399 | 1440 | 619 | 2.5261 | 47.1 | 55.1 | 23.5 | 5.3
1357015 |  |  | 1 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 823 | 1071 | 1150 | 1521 | 71 | 92 | 99 | 131 | 0.026344 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1029 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1 | [13 empty] | 0 | 100% | 100% | 100% | 100% | 100% | 100% | #REF! | T21 | [6 empty] | 220 | 0 | 4239 | 365 | 0.93691 |  |  |  | 0 | 0 | 0 | 5.9
1507015 |  |  | 1 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1214 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1 | [28 empty] | 220 | 10 | 8103 | 697 | 3.257 | 1051 | 452 | 1.4133 | 26 | 34 | 15.5 | 5.9
1657015 |  |  | 1 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1345 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1 | [28 empty] | 220 | 11.1 | 8440 | 726 | 3.5238 | 1095 | 471 | 1.5298 | 30 | 38 | 16.8 | 5.9
1957015 |  |  | 1 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1502 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1 | [28 empty] | 220 | 21.85 | 12318 | 1059 | 7.3137 | 1598 | 687 | 3.1674 | 47.8 | 55.8 | 27.5 | 5.9
1357016 |  |  | 1 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 758.2 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 758 | 1628 | 1747 | 2313 | 65 | 140 | 150 | 199 | 0.063729 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1115 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1 | [13 empty] | Lengths | Calculation factors for lower fan settings | [13 empty] | 240 | 0 | 4958 | 426 | 1.2947 |  |  |  | 0 | 0 | 0 | 6.4
1507016 |  |  | 1 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 904 | 1628 | 1747 | 2313 | 78 | 140 | 150 | 199 | 0.091342 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1329 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1 | [14 empty] | T10 |  | T11 |  | T15 |  | T16 |  | T20 |  | T21 |  |  |  | 240 | 10 | 8907 | 766 | 4.0011 | 1155 | 497 | 1.7405 | 26 | 34 | 16.4 | 6.4
1657016 |  |  | 1 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1034.28 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1034 | 1628 | 1747 | 2313 | 89 | 140 | 150 | 199 | 0.11854 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.1279 | 218.0533 | 288.6 | 0.95 | 0.95 | 0.95 | 203 | 218 | 289 | 87 | 94 | 124 | 0.11333 | 0.13205 | 0.22833 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1521 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 203 | 218 | 289 |  | 0 | 0 | 0 | 1 | [14 empty] | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 | S2 | S1 |  |  | 240 | 10.9 | 9231 | 794 | 4.2878 | 1197 | 515 | 1.8637 | 30 | 38 | 17.7 | 6.4
1957016 |  |  | 1 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1274.32 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1274 | 1628 | 1747 | 2313 | 110 | 140 | 150 | 199 | 0.18017 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 170.1882 | 182.6933 | 241.8 | 0.95 | 0.95 | 0.95 | 170 | 183 | 242 | 73 | 79 | 104 | 0.080141 | 0.093669 | 0.16126 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1874 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 170 | 183 | 242 |  | 0 | 0 | 0 | 1 | [13 empty] | 50 | 0.85519 | 0.79918 | 0.85519 | 0.79918 | [10 empty] | 240 | 21.85 | 13538 | 1164 | 8.9741 | 1756 | 755 | 3.8911 | 48.1 | 56.1 | 29.7 | 6.4
1357020 |  |  | 1 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1153.6 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1154 | 1510 | 1619 | 1936 | 99 | 130 | 139 | 166 | 0.039971 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1442 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1 | [13 empty] | 60 | 0.84525 | 0.7893 | 0.84525 | 0.7893 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.84525 | 0.7893 | 0.75556 | 0.70384 |  |  | 260 | 0 | 5134 | 442 | 1.4256 |  |  |  | 0 | 0 | 0 | 6.9
1507020 |  |  | 1 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1358 | 1510 | 1619 | 1936 | 117 | 130 | 139 | 166 | 0.055586 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1698 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1 | [13 empty] | 70 | 0.8364 | 0.77994 | 0.8364 | 0.77994 | 0.75556 | 0.70384 | 0.75556 | 0.70384 | 0.8364 | 0.77994 | 0.75556 | 0.70384 |  |  | 260 | 10 | 9235 | 794 | 4.3863 | 1168 | 502 | 1.8191 | 26 | 34 | 16.4 | 6.9
1657020 |  |  | 1 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1880 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1 | [13 empty] | 80 | 0.82846 | 0.77134 | 0.82846 | 0.77134 | 0.74531 | 0.69504 | 0.74531 | 0.69504 | 0.82846 | 0.77134 | 0.74531 | 0.69504 |  |  | 260 | 10.9 | 9571 | 823 | 4.6996 | 1210 | 520 | 1.9461 | 30 | 38 | 17.7 | 6.9
1957020 |  |  | 1 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 2094 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1 | [13 empty] | 90 | 0.82124 | 0.76344 | 0.82124 | 0.76344 | 0.7343 | 0.6854 | 0.7343 | 0.6854 | 0.82124 | 0.76344 | 0.7343 | 0.6854 |  |  | 260 | 21.85 | 14035 | 1207 | 9.8288 | 1774 | 763 | 4.0629 | 48.1 | 56.1 | 29.7 | 6.9
1357021 |  |  | 1 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1184 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1184 | 1978 | 2123 | 2810 | 102 | 170 | 183 | 242 | 0.060423 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1480 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1 | [13 empty] | 100 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746 |  |  | 280 | 0 | 5784 | 497 | 1.8285 |  |  |  | 0 | 0 | 0 | 7.5
1507021 |  |  | 1 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1446 | 1978 | 2123 | 2810 | 124 | 170 | 183 | 242 | 0.088673 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1807 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1 | [13 empty] | 110 | 0.81467 | 0.7562 | 0.81467 | 0.7562 | 0.72541 | 0.67746 | 0.72541 | 0.67746 | 0.81467 | 0.7562 | 0.72541 | 0.67746 |  |  | 280 | 10 | 10516 | 904 | 5.7534 | 1364 | 587 | 2.5138 | 26 | 34 | 19.3 | 7.5
1657021 |  |  | 1 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1696.8 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1697 | 1978 | 2123 | 2810 | 146 | 170 | 183 | 242 | 0.12224 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.2818 | 238.6146 | 315.8135 | 0.85 | 0.85 | 0.85 | 222 | 239 | 316 | 95 | 103 | 136 | 0.052552 | 0.061591 | 0.10633 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2121 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 222 | 239 | 316 |  | 0 | 0 | 0 | 1 | [13 empty] | 120 | 0.80301 | 0.7433 | 0.80301 | 0.7433 | 0.71879 | 0.67123 | 0.71879 | 0.67123 | 0.80301 | 0.7433 | 0.71879 | 0.67123 |  |  | 280 | 10.6 | 10751 | 925 | 6.0129 | 1395 | 600 | 2.6215 | 30 | 38 | 20.4 | 7.5
1957021 |  |  | 1 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1883 | 1978 | 2123 | 2810 | 162 | 170 | 183 | 242 | 0.14998 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 186.2361 | 199.9203 | 264.6005 | 0.85 | 0.85 | 0.85 | 186 | 200 | 265 | 80 | 86 | 114 | 0.037513 | 0.043229 | 0.075172 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2744 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 186 | 200 | 265 |  | 0 | 0 | 0 | 1 | [13 empty] | 140 | 0.79292 | 0.73212 | 0.79292 | 0.73212 | 0.71271 | 0.66551 | 0.71271 | 0.66551 | 0.79292 | 0.73212 | 0.71271 | 0.66551 |  |  | 280 | 21.85 | 15977 | 1374 | 12.8758 | 2072 | 891 | 5.5955 | 48.9 | 56.9 | 34.5 | 7.5
1358010 |  |  | 1 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 646.2 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 646 | 1214 | 1304 | 1574 | 56 | 104 | 112 | 135 | 0.016788 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 718 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1 | [13 empty] | 160 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707 |  |  | 300 | #N/A | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | #N/A
1508010 |  |  | 1 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 775 | 1214 | 1304 | 1574 | 67 | 104 | 112 | 135 | 0.023665 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 861 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1 | [13 empty] | 180 | 0.78402 | 0.72224 | 0.78402 | 0.72224 | 0.70153 | 0.65707 | 0.70153 | 0.65707 | 0.78402 | 0.72224 | 0.70153 | 0.65707 |  |  | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1658010 |  |  | 1 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 872.1 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 872 | 1214 | 1304 | 1574 | 75 | 104 | 112 | 135 | 0.029377 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 969 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1 | [13 empty] | 200 | 0.76886 | 0.70539 | 0.76886 | 0.70539 | 0.69292 | 0.65762 | 0.69292 | 0.65762 | 0.76886 | 0.70539 | 0.69292 | 0.65762 |  |  | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1958010 |  |  | 1 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1002.6 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1003 | 1214 | 1304 | 1574 | 86 | 104 | 112 | 135 | 0.038198 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 1114 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1 | [13 empty] | 220 | 0.75856 | 0.69426 | 0.75856 | 0.69426 | 0.68521 | 0.65781 | 0.68521 | 0.65781 | 0.75856 | 0.69426 | 0.68521 | 0.65781 |  |  | 300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1358011 |  |  | 1 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 650.76 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 651 | 1648 | 1770 | 2136 | 56 | 142 | 152 | 184 | 0.028647 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 957 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1 | [13 empty] | 240 | 0.75028 | 0.68489 | 0.75028 | 0.68489 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75028 | 0.68489 | 0.6819 | 0.65797 | [13 empty] | v2020-09-17
1508011 |  |  | 1 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 754 | 1648 | 1770 | 2136 | 65 | 142 | 152 | 184 | 0.03802 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1109 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1 | [13 empty] | 260 | 0.75 | 0.68 | 0.75 | 0.68 | 0.6819 | 0.65797 | 0.6819 | 0.65797 | 0.75 | 0.68 | 0.6819 | 0.65797 |  |  | * | 0
1658011 |  |  | 1 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 839.12 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 839 | 1648 | 1770 | 2136 | 72 | 142 | 152 | 184 | 0.046182 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255.3 | 273.8 | 331.15 | 0.95 | 0.95 | 0.95 | 255 | 274 | 331 | 110 | 118 | 142 | 0.10357 | 0.11843 | 0.16872 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1234 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 255 | 274 | 331 |  | 0 | 0 | 0 | 1 | [13 empty] | 280 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821 |  |  | ** | 0
1958011 |  |  | 1 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 977.16 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 977 | 1648 | 1770 | 2136 | 84 | 142 | 152 | 184 | 0.06193 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 213.9 | 229.4 | 277.45 | 0.95 | 0.95 | 0.95 | 214 | 229 | 277 | 92 | 98 | 119 | 0.073653 | 0.083082 | 0.12035 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1437 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 214 | 229 | 277 |  | 0 | 0 | 0 | 1 | [13 empty] | 300 | 0.75078 | 0.68 | 0.75078 | 0.68 | 0.67294 | 0.65821 | 0.67294 | 0.65821 | 0.75078 | 0.68 | 0.67294 | 0.65821 |  |  | *** | 0
1358015 |  |  | 1 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 940.8 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 941 | 1395 | 1496 | 2008 | 81 | 120 | 129 | 173 | 0.034919 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1176 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1 | [28 empty] | **** | 0
1508015 |  |  | 1 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1110 | 1395 | 1496 | 2008 | 95 | 120 | 129 | 173 | 0.047724 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1 | [13 empty] | Type,ww | L/cm
1658015 |  |  | 1 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1230.4 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1230 | 1395 | 1496 | 2008 | 106 | 120 | 129 | 173 | 0.059161 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1538 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1 | [13 empty] | 10 | 0.0066667
1958015 |  |  | 1 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1300.3374 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1300 | 1395 | 1496 | 2008 | 112 | 120 | 129 | 173 | 0.065908 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1717 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1 | [13 empty] | 11 | 0.013333
1358016 |  |  | 1 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 866.32 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 866 | 2040 | 2188 | 2936 | 74 | 175 | 188 | 252 | 0.083686 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1274 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1 | [13 empty] | 15 | 0.01
1508016 |  |  | 1 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1032 | 2040 | 2188 | 2936 | 89 | 175 | 188 | 252 | 0.12041 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1 | [13 empty] | 16 | 0.02
1658016 |  |  | 1 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1181.84 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1182 | 2040 | 2188 | 2936 | 102 | 175 | 188 | 252 | 0.15756 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 288.6 | 309.875 | 416.25 | 0.95 | 0.95 | 0.95 | 289 | 310 | 416 | 124 | 133 | 179 | 0.23165 | 0.26601 | 0.47834 | 1.6 | 6 | 6.7 | 9 |  | 1738 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 289 | 310 | 416 |  | 0 | 0 | 0 | 1 | [13 empty] | 20 | 0.013333
1958016 |  |  | 1 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1456.56 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1457 | 2040 | 2188 | 2936 | 125 | 175 | 188 | 252 | 0.23535 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 241.8 | 259.625 | 348.75 | 0.95 | 0.95 | 0.95 | 242 | 260 | 349 | 104 | 112 | 150 | 0.16371 | 0.18949 | 0.33734 | 1.6 | 6 | 6.7 | 9 |  | 2142 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 242 | 260 | 349 |  | 0 | 0 | 0 | 1 | [13 empty] | 21 | 0.026667
1358020 |  |  | 1 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1318.4 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1318 | 1943 | 2086 | 2518 | 113 | 167 | 179 | 217 | 0.052754 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1648 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
1508020 |  |  | 1 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1552 | 1943 | 2086 | 2518 | 133 | 167 | 179 | 217 | 0.072735 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
1658020 |  |  | 1 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1718.4 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1718 | 1943 | 2086 | 2518 | 148 | 167 | 179 | 217 | 0.089796 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2148 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1 | [13 empty] | Niveaus | Type | k1 | n | t | k2
1958020 |  |  | 1 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1847.5719 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1848 | 1943 | 2086 | 2518 | 159 | 167 | 179 | 217 | 0.10344 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2394 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
1358021 |  |  | 1 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1352.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1353 | 2628 | 2818 | 3781 | 116 | 226 | 242 | 325 | 0.079579 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 1691 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 row
1508021 |  |  | 1 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1653 | 2628 | 2818 | 3781 | 142 | 226 | 242 | 325 | 0.11828 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 4 | 0.0013823 | 1.7232 | 1 | 0.00033291
1658021 |  |  | 1 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1939.2 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1939 | 2628 | 2818 | 3781 | 167 | 226 | 242 | 325 | 0.16258 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315.2976 | 338.1017 | 453.6385 | 0.85 | 0.85 | 0.85 | 315 | 338 | 454 | 135 | 145 | 195 | 0.10712 | 0.12323 | 0.22041 | 2.1 | 6 | 6.7 | 9 |  | 2424 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 315 | 338 | 454 |  | 0 | 0 | 0 | 1 | [13 empty] | 2 | 5 | 0.000937 | 1.789 | 2 | 0.000446
1958021 |  |  | 1 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2508.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 2509 | 2628 | 2818 | 3781 | 216 | 226 | 242 | 325 | 0.26944 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264.1682 | 283.2744 | 380.0755 | 0.85 | 0.85 | 0.85 | 264 | 283 | 380 | 114 | 122 | 163 | 0.076913 | 0.087842 | 0.15503 | 2.1 | 6 | 6.7 | 9 |  | 3136 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 380 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 | 6 | 0.000937 | 1.789 | 4 | 0.00139
1359010 |  |  | 1 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 727.2 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 727 | 1396 | 1501 | 1828 | 63 | 120 | 129 | 157 | 0.022062 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 808 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1 | [13 empty] | 2 rows
1509010 |  |  | 1 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 871 | 1396 | 1501 | 1828 | 75 | 120 | 129 | 157 | 0.030768 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 968 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 9 | 0.00080534 | 1.8139 | 2 | 0.00039795
1659010 |  |  | 1 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 981 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 981 | 1396 | 1501 | 1828 | 84 | 120 | 129 | 157 | 0.038205 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1090 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1 | [13 empty] | 2 | 10 | 0.0003969 | 1.7346 | 2 | 0.00036735
1959010 |  |  | 1 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1128.6 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 1129 | 1396 | 1501 | 1828 | 97 | 120 | 129 | 157 | 0.050305 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1254 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 | 11 | 0.0003969 | 1.7346 | 4 | 0.00057429
1359011 |  |  | 1 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 731.68 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 732 | 1894 | 2037 | 2480 | 63 | 163 | 175 | 213 | 0.037884 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1076 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1 | [13 empty] | 3 rows
1509011 |  |  | 1 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 848 | 1894 | 2037 | 2480 | 73 | 163 | 175 | 213 | 0.050065 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1247 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 14 | 0.0025582 | 1.4943 | 3 | 0.00056162
1659011 |  |  | 1 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 944.52 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 945 | 1894 | 2037 | 2480 | 81 | 163 | 175 | 213 | 0.060966 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 293.3758 | 315.5893 | 384.282 | 0.95 | 0.95 | 0.95 | 293 | 316 | 384 | 126 | 136 | 165 | 0.14109 | 0.16316 | 0.23581 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1389 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 293 | 316 | 384 |  | 0 | 0 | 0 | 1 | [13 empty] | 2 | 15 | 0.0002083 | 1.724 | 2 | 0.00046183
1959011 |  |  | 1 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1098.88 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1099 | 1894 | 2037 | 2480 | 95 | 163 | 175 | 213 | 0.082492 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 245.8013 | 264.4127 | 321.966 | 0.95 | 0.95 | 0.95 | 246 | 264 | 322 | 106 | 114 | 138 | 0.10157 | 0.11663 | 0.16776 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1616 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 246 | 264 | 322 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 | 16 | 0.0002083 | 1.724 | 4 | 0.0013928
1359015 |  |  | 1 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1058.4 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1058 | 1598 | 1712 | 2331 | 91 | 137 | 147 | 200 | 0.044839 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1323 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 rows
1509015 |  |  | 1 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1249 | 1598 | 1712 | 2331 | 107 | 137 | 147 | 200 | 0.061548 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1561 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 19 | 0.011616 | 1.5869 | 1 | 0.0016553
1659015 |  |  | 1 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1384 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1384 | 1598 | 1712 | 2331 | 119 | 137 | 147 | 200 | 0.075779 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1730 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1 | [13 empty] | 2 | 20 | 0.0001276 | 1.7219 | 2 | 0.00037661
1959015 |  |  | 1 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1502.9168 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1503 | 1598 | 1712 | 2331 | 129 | 137 | 147 | 200 | 0.088747 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1931 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 | 21 | 0.0001276 | 1.7219 | 4 | 0.0005142
1359016 |  |  | 1 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 975.12 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 975 | 2337 | 2503 | 3409 | 84 | 201 | 215 | 293 | 0.10913 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1434 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
1509016 |  |  | 1 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1161 | 2337 | 2503 | 3409 | 100 | 201 | 215 | 293 | 0.15381 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1708 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1 | [13 empty] | 1 | 7 | 0.0025582 | 1.4943 | 3 | 0.00056162
1659016 |  |  | 1 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1330.08 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1330 | 2337 | 2503 | 3409 | 114 | 201 | 215 | 293 | 0.19909 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 330.9459 | 354.5558 | 482.85 | 0.95 | 0.95 | 0.95 | 331 | 355 | 483 | 142 | 153 | 208 | 0.30693 | 0.35557 | 0.65174 | 1.8 | 7 | 7.7 | 10.7 |  | 1956 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 331 | 355 | 483 |  | 0 | 0 | 0 | 1 | [13 empty] | 4 | 8 | 0.000937 | 1.789 | 4 | 0.00139
1959016 |  |  | 1 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1638.12 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1638 | 2337 | 2503 | 3409 | 141 | 201 | 215 | 293 | 0.30268 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277.279 | 297.0603 | 404.55 | 0.95 | 0.95 | 0.95 | 277 | 297 | 405 | 119 | 128 | 174 | 0.21666 | 0.25014 | 0.45825 | 1.8 | 7 | 7.7 | 10.7 |  | 2409 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 277 | 297 | 405 |  | 0 | 0 | 0 | 1
1359020 |  |  | 1 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1483.2 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1483 | 2233 | 2402 | 2925 | 128 | 192 | 207 | 252 | 0.068506 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1854 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
1509020 |  |  | 1 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1746 | 2233 | 2402 | 2925 | 150 | 192 | 207 | 252 | 0.093602 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2183 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
1659020 |  |  | 1 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1933.6 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1934 | 2233 | 2402 | 2925 | 166 | 192 | 207 | 252 | 0.11428 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2417 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
1959020 |  |  | 1 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2137.7837 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2138 | 2233 | 2402 | 2925 | 184 | 192 | 207 | 252 | 0.13997 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2693 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
1359021 |  |  | 1 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1522.4 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1522 | 3009 | 3224 | 4391 | 131 | 259 | 277 | 378 | 0.1032 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 1903 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
1509021 |  |  | 1 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1859 | 3009 | 3224 | 4391 | 160 | 259 | 277 | 378 | 0.1526 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 2324 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
1659021 |  |  | 1 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2181.6 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2182 | 3009 | 3224 | 4391 | 188 | 259 | 277 | 378 | 0.20926 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 361.0734 | 386.8326 | 526.806 | 0.85 | 0.85 | 0.85 | 361 | 387 | 527 | 155 | 166 | 227 | 0.14341 | 0.16401 | 0.30277 | 2.4 | 7 | 7.7 | 10.7 |  | 2727 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 361 | 387 | 527 |  | 0 | 0 | 0 | 1
1959021 |  |  | 1 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2822.4 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2822 | 3009 | 3224 | 4391 | 243 | 259 | 277 | 378 | 0.34602 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 302.521 | 324.103 | 441.378 | 0.85 | 0.85 | 0.85 | 303 | 324 | 441 | 130 | 139 | 190 | 0.10167 | 0.11588 | 0.21364 | 2.4 | 7 | 7.7 | 10.7 |  | 3528 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 441 |  | 0 | 0 | 0 | 1
13510010 |  |  | 1 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 808.2 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 808 | 1574 | 1696 | 2082 | 69 | 135 | 146 | 179 | 0.027445 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 898 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
15010010 |  |  | 1 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 968 | 1574 | 1696 | 2082 | 83 | 135 | 146 | 179 | 0.038999 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1076 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
16510010 |  |  | 1 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1089.9 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1090 | 1574 | 1696 | 2082 | 94 | 135 | 146 | 179 | 0.049429 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1211 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
19510010 |  |  | 1 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1253.7 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1254 | 1574 | 1696 | 2082 | 108 | 135 | 146 | 179 | 0.064408 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1393 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
13510011 |  |  | 1 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 813.28 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 813 | 2136 | 2301 | 2825 | 70 | 184 | 198 | 243 | 0.04871 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1196 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
15010011 |  |  | 1 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 942 | 2136 | 2301 | 2825 | 81 | 184 | 198 | 243 | 0.064146 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1386 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
16510011 |  |  | 1 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1049.24 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1049 | 2136 | 2301 | 2825 | 90 | 184 | 198 | 243 | 0.078266 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 331.15 | 356.125 | 437.525 | 0.95 | 0.95 | 0.95 | 331 | 356 | 438 | 142 | 153 | 188 | 0.18556 | 0.21378 | 0.31619 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1543 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 331 | 356 | 438 |  | 0 | 0 | 0 | 1
19510011 |  |  | 1 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1221.28 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1221 | 2136 | 2301 | 2825 | 105 | 184 | 198 | 243 | 0.10475 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277.45 | 298.375 | 366.575 | 0.95 | 0.95 | 0.95 | 277 | 298 | 367 | 119 | 128 | 158 | 0.13275 | 0.15241 | 0.22724 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1796 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 277 | 298 | 367 |  | 0 | 0 | 0 | 1
13510015 |  |  | 1 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1176 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1176 | 1799 | 1926 | 2655 | 101 | 155 | 166 | 228 | 0.056143 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1470 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
15010015 |  |  | 1 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1387 | 1799 | 1926 | 2655 | 119 | 155 | 166 | 228 | 0.077325 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1734 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
16510015 |  |  | 1 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1537.6 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1538 | 1799 | 1926 | 2655 | 132 | 155 | 166 | 228 | 0.094683 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1922 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
19510015 |  |  | 1 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1703.7737 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1704 | 1799 | 1926 | 2655 | 147 | 155 | 166 | 228 | 0.11685 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 2146 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
13510016 |  |  | 1 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1083.24 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1083 | 2630 | 2817 | 3883 | 93 | 226 | 242 | 334 | 0.13536 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1593 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
15010016 |  |  | 1 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1291 | 2630 | 2817 | 3883 | 111 | 226 | 242 | 334 | 0.19165 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1898 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
16510016 |  |  | 1 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1477.64 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1478 | 2630 | 2817 | 3883 | 127 | 226 | 242 | 334 | 0.24976 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 372.775 | 398.675 | 550.375 | 0.95 | 0.95 | 0.95 | 373 | 399 | 550 | 160 | 172 | 237 | 0.39352 | 0.45375 | 0.85347 | 2 | 7 | 7.7 | 10.7 |  | 2173 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 373 | 399 | 550 |  | 0 | 0 | 0 | 1
19510016 |  |  | 1 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1820.36 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1820 | 2630 | 2817 | 3883 | 157 | 226 | 242 | 334 | 0.37912 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312.325 | 334.025 | 461.125 | 0.95 | 0.95 | 0.95 | 312 | 334 | 461 | 134 | 144 | 198 | 0.27757 | 0.3198 | 0.59878 | 2 | 7 | 7.7 | 10.7 |  | 2677 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 312 | 334 | 461 |  | 0 | 0 | 0 | 1
13510020 |  |  | 1 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1648 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1648 | 2519 | 2714 | 3331 | 142 | 217 | 233 | 286 | 0.0853 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2060 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
15010020 |  |  | 1 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1940 | 2519 | 2714 | 3331 | 167 | 217 | 233 | 286 | 0.11732 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2425 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
16510020 |  |  | 1 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2148 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2148 | 2519 | 2714 | 3331 | 185 | 217 | 233 | 286 | 0.14347 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2685 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
19510020 |  |  | 1 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2393.6 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2394 | 2519 | 2714 | 3331 | 206 | 217 | 233 | 286 | 0.17727 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2992 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
13510021 |  |  | 1 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 1691 | 3388 | 3627 | 5000 | 145 | 291 | 312 | 430 | 0.1285 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2114 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
15010021 |  |  | 1 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2066 | 3388 | 3627 | 5000 | 178 | 291 | 312 | 430 | 0.19177 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2582 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
16510021 |  |  | 1 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2424 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2424 | 3388 | 3627 | 5000 | 208 | 291 | 312 | 430 | 0.26 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 406.4601 | 435.2289 | 599.9735 | 0.85 | 0.85 | 0.85 | 406 | 435 | 600 | 175 | 187 | 258 | 0.18551 | 0.21117 | 0.39627 | 2.7 | 7 | 7.7 | 10.7 |  | 3030 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 406 | 435 | 600 |  | 0 | 0 | 0 | 1
19510021 |  |  | 1 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3136 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3136 | 3388 | 3627 | 5000 | 270 | 291 | 312 | 430 | 0.43315 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.5476 | 364.6513 | 502.6805 | 0.85 | 0.85 | 0.85 | 341 | 365 | 503 | 147 | 157 | 216 | 0.13199 | 0.15008 | 0.27991 | 2.7 | 7 | 7.7 | 10.7 |  | 3920 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 503 |  | 0 | 0 | 0 | 1
13511010 |  |  | 1 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 889.2 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 889 | 1766 | 1903 | 2336 | 76 | 152 | 164 | 201 | 0.034403 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 988 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
15011010 |  |  | 1 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1066 | 1766 | 1903 | 2336 | 92 | 152 | 164 | 201 | 0.049428 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1184 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
16511010 |  |  | 1 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1198.8 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1199 | 1766 | 1903 | 2336 | 103 | 152 | 164 | 201 | 0.061253 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1332 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
19511010 |  |  | 1 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1378.8 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1379 | 1766 | 1903 | 2336 | 119 | 152 | 164 | 201 | 0.080603 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1532 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
13511011 |  |  | 1 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 894.88 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 895 | 2397 | 2582 | 3169 | 77 | 206 | 222 | 273 | 0.061213 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1316 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
15011011 |  |  | 1 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1037 | 2397 | 2582 | 3169 | 89 | 206 | 222 | 273 | 0.080376 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1525 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
16511011 |  |  | 1 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1153.96 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1154 | 2397 | 2582 | 3169 | 99 | 206 | 222 | 273 | 0.098218 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 371.314 | 400.0249 | 491.027 | 0.95 | 0.95 | 0.95 | 371 | 400 | 491 | 160 | 172 | 211 | 0.24309 | 0.27875 | 0.41057 | 1.5 | 8.4 | 9.3 | 14 |  | 1697 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 371 | 400 | 491 |  | 0 | 0 | 0 | 1
19511011 |  |  | 1 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1343.68 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1344 | 2397 | 2582 | 3169 | 116 | 206 | 222 | 273 | 0.13241 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 311.1009 | 335.156 | 411.401 | 0.95 | 0.95 | 0.95 | 311 | 335 | 411 | 134 | 144 | 177 | 0.17385 | 0.19918 | 0.29429 | 1.5 | 8.4 | 9.3 | 14 |  | 1976 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 411 |  | 0 | 0 | 0 | 1
13511015 |  |  | 1 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1293.6 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1294 | 1908 | 2043 | 2817 | 111 | 164 | 176 | 242 | 0.068872 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1617 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
15011015 |  |  | 1 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1526 | 1908 | 2043 | 2817 | 131 | 164 | 176 | 242 | 0.095111 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1907 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
16511015 |  |  | 1 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1691.2 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1691 | 1908 | 2043 | 2817 | 145 | 164 | 176 | 242 | 0.11594 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2114 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
19511015 |  |  | 1 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1813.1502 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1813 | 1908 | 2043 | 2817 | 156 | 164 | 176 | 242 | 0.13371 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2361 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
13511016 |  |  | 1 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1191.36 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1191 | 2850 | 3051 | 4207 | 102 | 245 | 262 | 362 | 0.16467 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 1752 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
15011016 |  |  | 1 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1420 | 2850 | 3051 | 4207 | 122 | 245 | 262 | 362 | 0.23401 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2088 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
16511016 |  |  | 1 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1625.2 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1625 | 2850 | 3051 | 4207 | 140 | 245 | 262 | 362 | 0.30664 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 377.2455 | 403.9466 | 556.85 | 0.95 | 0.95 | 0.95 | 377 | 404 | 557 | 162 | 174 | 240 | 0.40852 | 0.47015 | 0.88527 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2390 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 377 | 404 | 557 |  | 0 | 0 | 0 | 1
19511016 |  |  | 1 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2002.6 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2003 | 2850 | 3051 | 4207 | 172 | 245 | 262 | 362 | 0.45958 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 316.0705 | 338.4417 | 466.55 | 0.95 | 0.95 | 0.95 | 316 | 338 | 467 | 136 | 145 | 201 | 0.28967 | 0.32853 | 0.62442 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2945 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 316 | 338 | 467 |  | 0 | 0 | 0 | 1
13511020 |  |  | 1 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1812.8 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1813 | 2693 | 2901 | 3561 | 156 | 232 | 249 | 306 | 0.1041 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2266 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
15011020 |  |  | 1 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2134 | 2693 | 2901 | 3561 | 184 | 232 | 249 | 306 | 0.14394 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2668 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
16511020 |  |  | 1 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2363.2 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2363 | 2693 | 2901 | 3561 | 203 | 232 | 249 | 306 | 0.17458 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2954 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
19511020 |  |  | 1 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2597.5513 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2598 | 2693 | 2901 | 3561 | 223 | 232 | 249 | 306 | 0.20997 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 3291 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
13511021 |  |  | 1 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1860 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 1860 | 3556 | 3808 | 5249 | 160 | 306 | 327 | 451 | 0.15885 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2325 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
15011021 |  |  | 1 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2272 | 3556 | 3808 | 5249 | 195 | 306 | 327 | 451 | 0.23357 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2840 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
16511021 |  |  | 1 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2666.4 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2666 | 3556 | 3808 | 5249 | 229 | 306 | 327 | 451 | 0.31959 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 412.2253 | 441.4022 | 608.4835 | 0.85 | 0.85 | 0.85 | 412 | 441 | 608 | 177 | 190 | 261 | 0.19338 | 0.22204 | 0.41259 | 2.9 | 7.9 | 8.8 | 12.5 |  | 3333 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 412 | 441 | 608 |  | 0 | 0 | 0 | 1
19511021 |  |  | 1 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3449.6 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 3450 | 3556 | 3808 | 5249 | 297 | 306 | 327 | 451 | 0.53108 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345.378 | 369.8235 | 509.8105 | 0.85 | 0.85 | 0.85 | 345 | 370 | 510 | 148 | 159 | 219 | 0.13647 | 0.15692 | 0.29292 | 2.9 | 7.9 | 8.8 | 12.5 |  | 4312 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 345 | 370 | 510 |  | 0 | 0 | 0 | 1
13512010 |  |  | 1 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 970.2 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 970 | 1925 | 2080 | 2590 | 83 | 166 | 179 | 223 | 0.042316 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1078 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
15012010 |  |  | 1 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1162 | 1925 | 2080 | 2590 | 100 | 166 | 179 | 223 | 0.060199 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
16512010 |  |  | 1 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1307.7 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1308 | 1925 | 2080 | 2590 | 112 | 166 | 179 | 223 | 0.074614 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1453 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
19512010 |  |  | 1 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1504.8 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1505 | 1925 | 2080 | 2590 | 129 | 166 | 179 | 223 | 0.097546 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1672 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
13512011 |  |  | 1 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 975.8 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 976 | 2612 | 2822 | 3514 | 84 | 225 | 243 | 302 | 0.075479 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1435 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
15012011 |  |  | 1 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1131 | 2612 | 2822 | 3514 | 97 | 225 | 243 | 302 | 0.098862 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
16512011 |  |  | 1 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1259.36 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1259 | 2612 | 2822 | 3514 | 108 | 225 | 243 | 302 | 0.12096 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 404.225 | 437.525 | 544.825 | 0.95 | 0.95 | 0.95 | 404 | 438 | 545 | 174 | 188 | 234 | 0.29689 | 0.34359 | 0.51965 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1852 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 404 | 438 | 545 |  | 0 | 0 | 0 | 1
19512011 |  |  | 1 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1465.4 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1465 | 2612 | 2822 | 3514 | 126 | 225 | 243 | 302 | 0.16162 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 338.675 | 366.575 | 456.475 | 0.95 | 0.95 | 0.95 | 339 | 367 | 456 | 146 | 158 | 196 | 0.21327 | 0.24751 | 0.37172 | 1.6 | 8.9 | 9.9 | 14.8 |  | 2155 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 339 | 367 | 456 |  | 0 | 0 | 0 | 1
13512015 |  |  | 1 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1411.2 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1411 | 2217 | 2374 | 3303 | 121 | 191 | 204 | 284 | 0.083065 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1764 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
15012015 |  |  | 1 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1665 | 2217 | 2374 | 3303 | 143 | 191 | 204 | 284 | 0.11496 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2081 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
16512015 |  |  | 1 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1845 | 2217 | 2374 | 3303 | 159 | 191 | 204 | 284 | 0.14132 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2306 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
19512015 |  |  | 1 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2060 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2060 | 2217 | 2374 | 3303 | 177 | 191 | 204 | 284 | 0.17416 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2575 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
13512016 |  |  | 1 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1300.16 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1300 | 3242 | 3472 | 4830 | 112 | 279 | 299 | 415 | 0.20063 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 1912 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
15012016 |  |  | 1 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1549 | 3242 | 3472 | 4830 | 133 | 279 | 299 | 415 | 0.281 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2278 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
16512016 |  |  | 1 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1773.44 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1773 | 3242 | 3472 | 4830 | 152 | 279 | 299 | 415 | 0.36515 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 458.8 | 492.1 | 684.5 | 0.95 | 0.95 | 0.95 | 459 | 492 | 685 | 197 | 212 | 295 | 0.60758 | 0.70182 | 1.344 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2608 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 685 |  | 0 | 0 | 0 | 1
19512016 |  |  | 1 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2184.16 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2184 | 3242 | 3472 | 4830 | 188 | 279 | 299 | 415 | 0.55425 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 384.4 | 412.3 | 573.5 | 0.95 | 0.95 | 0.95 | 384 | 412 | 574 | 165 | 177 | 247 | 0.42896 | 0.49236 | 0.94772 | 2.4 | 8.7 | 9.8 | 14.3 |  | 3212 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 574 |  | 0 | 0 | 0 | 1
13512020 |  |  | 1 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1977.6 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 1978 | 3080 | 3327 | 4143 | 170 | 265 | 286 | 356 | 0.12496 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2472 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
15012020 |  |  | 1 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2328 | 3080 | 3327 | 4143 | 200 | 265 | 286 | 356 | 0.17184 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2910 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
16512020 |  |  | 1 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2577.6 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2578 | 3080 | 3327 | 4143 | 222 | 265 | 286 | 356 | 0.21087 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3222 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
19512020 |  |  | 1 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2872 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2872 | 3080 | 3327 | 4143 | 247 | 265 | 286 | 356 | 0.25999 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3590 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
13512021 |  |  | 1 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2029.6 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2030 | 4175 | 4471 | 6220 | 175 | 359 | 385 | 535 | 0.19279 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 2537 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
15012021 |  |  | 1 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2478 | 4175 | 4471 | 6220 | 213 | 359 | 385 | 535 | 0.28258 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3098 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
16512021 |  |  | 1 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2908.8 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2909 | 4175 | 4471 | 6220 | 250 | 359 | 385 | 535 | 0.38604 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 500.9437 | 536.44 | 746.3085 | 0.85 | 0.85 | 0.85 | 501 | 536 | 746 | 215 | 230 | 321 | 0.28777 | 0.32815 | 0.62857 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3636 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 501 | 536 | 746 |  | 0 | 0 | 0 | 1
19512021 |  |  | 1 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3763.2 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3763 | 4175 | 4471 | 6220 | 324 | 359 | 385 | 535 | 0.64009 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 419.7096 | 449.4497 | 625.2855 | 0.85 | 0.85 | 0.85 | 420 | 449 | 625 | 181 | 193 | 269 | 0.20585 | 0.23323 | 0.44529 | 3.2 | 8.7 | 9.8 | 14.3 |  | 4704 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 420 | 449 | 625 |  | 0 | 0 | 0 | 1
13514010 |  |  | 1 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1131.3 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1131 | 2268 | 2456 | 3098 | 97 | 195 | 211 | 266 | 0.061174 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1257 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
15014010 |  |  | 1 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1355 | 2268 | 2456 | 3098 | 117 | 195 | 211 | 266 | 0.087073 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1506 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
16514010 |  |  | 1 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1525.5 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1526 | 2268 | 2456 | 3098 | 131 | 195 | 211 | 266 | 0.10776 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1695 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
19514010 |  |  | 1 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1755 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1755 | 2268 | 2456 | 3098 | 151 | 195 | 211 | 266 | 0.14091 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1950 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
13514011 |  |  | 1 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1138.32 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1138 | 3077 | 3333 | 4203 | 98 | 265 | 287 | 361 | 0.10963 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1674 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
15014011 |  |  | 1 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1319 | 3077 | 3333 | 4203 | 113 | 265 | 287 | 361 | 0.14302 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1940 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
16514011 |  |  | 1 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1468.8 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1469 | 3077 | 3333 | 4203 | 126 | 265 | 287 | 361 | 0.1753 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 476.375 | 516.15 | 651.2 | 0.95 | 0.95 | 0.95 | 476 | 516 | 651 | 205 | 222 | 280 | 0.43647 | 0.50695 | 0.78463 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2160 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 476 | 516 | 651 |  | 0 | 0 | 0 | 1
19514011 |  |  | 1 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1709.52 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1710 | 3077 | 3333 | 4203 | 147 | 265 | 287 | 361 | 0.23392 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 399.125 | 432.45 | 545.6 | 0.95 | 0.95 | 0.95 | 399 | 432 | 546 | 172 | 186 | 235 | 0.31397 | 0.36362 | 0.56421 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2514 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 399 | 432 | 546 |  | 0 | 0 | 0 | 1
13514015 |  |  | 1 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1646.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1646 | 2629 | 2815 | 3950 | 142 | 226 | 242 | 340 | 0.11759 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2058 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
15014015 |  |  | 1 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1942 | 2629 | 2815 | 3950 | 167 | 226 | 242 | 340 | 0.16105 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2428 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
16514015 |  |  | 1 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2152.8 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2153 | 2629 | 2815 | 3950 | 185 | 226 | 242 | 340 | 0.19645 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2691 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
19514015 |  |  | 1 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2403.2 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2403 | 2629 | 2815 | 3950 | 207 | 226 | 242 | 340 | 0.24436 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 3004 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
13514016 |  |  | 1 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1516.4 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1516 | 3844 | 4117 | 5777 | 130 | 331 | 354 | 497 | 0.2759 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2230 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
15014016 |  |  | 1 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1807 | 3844 | 4117 | 5777 | 155 | 331 | 354 | 497 | 0.38918 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2657 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
16514016 |  |  | 1 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2068.56 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2069 | 3844 | 4117 | 5777 | 178 | 331 | 354 | 497 | 0.51022 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 544.825 | 582.75 | 818.625 | 0.95 | 0.95 | 0.95 | 545 | 583 | 819 | 234 | 251 | 352 | 0.87198 | 1.0005 | 1.9431 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3042 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 545 | 583 | 819 |  | 0 | 0 | 0 | 1
19514016 |  |  | 1 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2548.64 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2549 | 3844 | 4117 | 5777 | 219 | 331 | 354 | 497 | 0.76578 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 456.475 | 488.25 | 685.875 | 0.95 | 0.95 | 0.95 | 456 | 488 | 686 | 196 | 210 | 295 | 0.61615 | 0.70533 | 1.3736 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3748 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 456 | 488 | 686 |  | 0 | 0 | 0 | 1
13514020 |  |  | 1 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2307.2 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2307 | 3628 | 3929 | 4956 | 198 | 312 | 338 | 426 | 0.17299 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 2884 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
15014020 |  |  | 1 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2716 | 3628 | 3929 | 4956 | 234 | 312 | 338 | 426 | 0.23982 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3395 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
16514020 |  |  | 1 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3007.2 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3007 | 3628 | 3929 | 4956 | 259 | 312 | 338 | 426 | 0.29251 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3759 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
19514020 |  |  | 1 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3351.2 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3351 | 3628 | 3929 | 4956 | 288 | 312 | 338 | 426 | 0.36007 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 4189 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
13514021 |  |  | 1 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2368 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2368 | 4951 | 5302 | 7440 | 204 | 426 | 456 | 640 | 0.26929 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 2960 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
15014021 |  |  | 1 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2892 | 4951 | 5302 | 7440 | 249 | 426 | 456 | 640 | 0.39641 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 3615 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
16514021 |  |  | 1 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3393.6 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3394 | 4951 | 5302 | 7440 | 292 | 426 | 456 | 640 | 0.54014 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 594.0588 | 636.1954 | 892.6435 | 0.85 | 0.85 | 0.85 | 594 | 636 | 893 | 255 | 273 | 384 | 0.41516 | 0.47396 | 0.9201 | 3.7 | 9.6 | 10.5 | 16.1 |  | 4242 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 594 | 636 | 893 |  | 0 | 0 | 0 | 1
19514021 |  |  | 1 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4390.4 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4390 | 4951 | 5302 | 7440 | 378 | 426 | 456 | 640 | 0.89233 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 497.7249 | 533.0285 | 747.8905 | 0.85 | 0.85 | 0.85 | 498 | 533 | 748 | 214 | 229 | 322 | 0.29547 | 0.33696 | 0.65322 | 3.7 | 9.6 | 10.5 | 16.1 |  | 5488 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 498 | 533 | 748 |  | 0 | 0 | 0 | 1
13516010 |  |  | 1 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1293.3 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1293 | 2604 | 2827 | 3605 | 111 | 224 | 243 | 310 | 0.084342 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1437 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
15016010 |  |  | 1 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1550 | 2604 | 2827 | 3605 | 133 | 224 | 243 | 310 | 0.1184 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1722 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
16516010 |  |  | 1 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1744.2 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1744 | 2604 | 2827 | 3605 | 150 | 224 | 243 | 310 | 0.14841 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1938 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
13516011 |  |  | 1 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1301.52 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1302 | 3533 | 3835 | 4892 | 112 | 304 | 330 | 421 | 0.15183 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 1914 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
15016011 |  |  | 1 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1508 | 3533 | 3835 | 4892 | 130 | 304 | 330 | 421 | 0.2003 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 2218 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
16516011 |  |  | 1 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1678.92 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1679 | 3533 | 3835 | 4892 | 144 | 304 | 330 | 421 | 0.24231 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.6 | 593.85 | 757.575 | 0.95 | 0.95 | 0.95 | 548 | 594 | 758 | 236 | 255 | 326 | 0.60938 | 0.70443 | 1.1164 | 2.1 | 11 | 12.4 | 19.2 |  | 2469 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 548 | 594 | 758 |  | 0 | 0 | 0 | 1
13516015 |  |  | 1 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1881.6 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1882 | 3021 | 3226 | 4598 | 162 | 260 | 277 | 395 | 0.15709 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2352 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
15016015 |  |  | 1 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2219 | 3021 | 3226 | 4598 | 191 | 260 | 277 | 395 | 0.216 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2774 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
16516015 |  |  | 1 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2460 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2460 | 3021 | 3226 | 4598 | 212 | 260 | 277 | 395 | 0.26433 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 3075 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
13516016 |  |  | 1 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1733.32 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1733 | 4418 | 4717 | 6724 | 149 | 380 | 406 | 578 | 0.36936 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 2549 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
15016016 |  |  | 1 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2065 | 4418 | 4717 | 6724 | 178 | 380 | 406 | 578 | 0.5226 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3037 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
16516016 |  |  | 1 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2364.36 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2364 | 4418 | 4717 | 6724 | 203 | 380 | 406 | 578 | 0.67553 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 625.3 | 667.85 | 952.75 | 0.95 | 0.95 | 0.95 | 625 | 668 | 953 | 269 | 287 | 410 | 1.1714 | 1.3297 | 2.6743 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3477 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 625 | 668 | 953 |  | 0 | 0 | 0 | 1
13516020 |  |  | 1 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2636.8 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 2637 | 4166 | 4522 | 5768 | 227 | 358 | 389 | 496 | 0.23169 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3296 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
15016020 |  |  | 1 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3104 | 4166 | 4522 | 5768 | 267 | 358 | 389 | 496 | 0.318 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3880 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
16516020 |  |  | 1 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3436.8 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3437 | 4166 | 4522 | 5768 | 296 | 358 | 389 | 496 | 0.38892 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 4296 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
13516021 |  |  | 1 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2705.6 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 2706 | 5690 | 6075 | 8659 | 233 | 489 | 522 | 745 | 0.3604 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 3382 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
15016021 |  |  | 1 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3305 | 5690 | 6075 | 8659 | 284 | 489 | 522 | 745 | 0.52853 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4131 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
16516021 |  |  | 1 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3878.4 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3878 | 5690 | 6075 | 8659 | 334 | 489 | 522 | 745 | 0.72356 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 682.6809 | 728.8758 | 1038.9785 | 0.85 | 0.85 | 0.85 | 683 | 729 | 1039 | 294 | 313 | 447 | 0.56515 | 0.63802 | 1.2735 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4848 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 683 | 729 | 1039 |  | 0 | 0 | 0 | 1
13518010 |  |  | 1 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1454.4 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1454 | 2971 | 3225 | 4113 | 125 | 256 | 277 | 354 | 0.11214 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1616 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
15018010 |  |  | 1 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1743 | 2971 | 3225 | 4113 | 150 | 256 | 277 | 354 | 0.15767 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1937 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
16518010 |  |  | 1 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1962 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1962 | 2971 | 3225 | 4113 | 169 | 256 | 277 | 354 | 0.19711 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 2180 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
13518011 |  |  | 1 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1464.04 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1464 | 4031 | 4376 | 5581 | 126 | 347 | 376 | 480 | 0.20268 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2153 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
15018011 |  |  | 1 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1697 | 4031 | 4376 | 5581 | 146 | 347 | 376 | 480 | 0.26629 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2495 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
16518011 |  |  | 1 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1888.36 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1888 | 4031 | 4376 | 5581 | 162 | 347 | 376 | 480 | 0.32295 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 624.4704 | 677.8928 | 864.6345 | 0.95 | 0.95 | 0.95 | 624 | 678 | 865 | 268 | 292 | 372 | 0.82386 | 0.96681 | 1.52 | 2.4 | 12.2 | 13.7 | 22 |  | 2777 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 624 | 678 | 865 |  | 0 | 0 | 0 | 1
13518015 |  |  | 1 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2116.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2117 | 3233 | 3452 | 4921 | 182 | 278 | 297 | 423 | 0.20317 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 2646 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
15018015 |  |  | 1 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2497 | 3233 | 3452 | 4921 | 215 | 278 | 297 | 423 | 0.28019 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3121 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
16518015 |  |  | 1 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2768 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2768 | 3233 | 3452 | 4921 | 238 | 278 | 297 | 423 | 0.34094 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3460 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
13518016 |  |  | 1 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1949.56 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 1950 | 4843 | 5171 | 7371 | 168 | 417 | 445 | 634 | 0.47802 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 2867 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
15018016 |  |  | 1 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2323 | 4843 | 5171 | 7371 | 200 | 417 | 445 | 634 | 0.67129 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3416 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
16518016 |  |  | 1 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2659.48 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2659 | 4843 | 5171 | 7371 | 229 | 417 | 445 | 634 | 0.87406 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 634.8357 | 677.7931 | 966.1625 | 0.95 | 0.95 | 0.95 | 635 | 678 | 966 | 273 | 292 | 415 | 1.2316 | 1.4044 | 2.7919 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3911 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 635 | 678 | 966 |  | 0 | 0 | 0 | 1
13518020 |  |  | 1 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2966.4 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2966 | 4498 | 4883 | 6228 | 255 | 387 | 420 | 536 | 0.29767 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 3708 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
15018020 |  |  | 1 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3492 | 4498 | 4883 | 6228 | 300 | 387 | 420 | 536 | 0.40847 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4365 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
16518020 |  |  | 1 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3866.4 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3866 | 4498 | 4883 | 6228 | 332 | 387 | 420 | 536 | 0.49766 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4833 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
13518021 |  |  | 1 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3044 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3044 | 6017 | 6424 | 9157 | 262 | 517 | 552 | 788 | 0.46677 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 3805 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
15018021 |  |  | 1 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3718 | 6017 | 6424 | 9157 | 320 | 517 | 552 | 788 | 0.68655 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 4648 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
16518021 |  |  | 1 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4363.2 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4363 | 6017 | 6424 | 9157 | 375 | 517 | 552 | 788 | 0.93272 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 693.8642 | 740.8158 | 1055.9985 | 0.85 | 0.85 | 0.85 | 694 | 741 | 1056 | 298 | 319 | 454 | 0.59835 | 0.68241 | 1.3501 | 4.8 | 11.5 | 12.8 | 19.6 |  | 5454 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 694 | 741 | 1056 |  | 0 | 0 | 0 | 1
13520010 |  |  | 1 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1616.4 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1616 | 3260 | 3553 | 4621 | 139 | 280 | 306 | 397 | 0.14485 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1796 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
15020010 |  |  | 1 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1937 | 3260 | 3553 | 4621 | 167 | 280 | 306 | 397 | 0.20392 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2152 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
16520010 |  |  | 1 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2179.8 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 2180 | 3260 | 3553 | 4621 | 187 | 280 | 306 | 397 | 0.25185 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2422 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
13520011 |  |  | 1 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1626.56 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1627 | 4423 | 4821 | 6270 | 140 | 380 | 415 | 539 | 0.26279 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2392 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
15020011 |  |  | 1 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1885 | 4423 | 4821 | 6270 | 162 | 380 | 415 | 539 | 0.34411 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2772 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
16520011 |  |  | 1 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2098.48 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2098 | 4423 | 4821 | 6270 | 180 | 380 | 415 | 539 | 0.41815 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 685.425 | 746.475 | 971.25 | 0.95 | 0.95 | 0.95 | 685 | 746 | 971 | 295 | 321 | 418 | 1.0453 | 1.2231 | 2.0002 | 2.7 | 13.4 | 14.8 | 24 |  | 3086 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 685 | 746 | 971 |  | 0 | 0 | 0 | 1
13520015 |  |  | 1 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2352 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2352 | 3875 | 4083 | 5893 | 202 | 333 | 351 | 507 | 0.25612 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 2940 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
15020015 |  |  | 1 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2774 | 3875 | 4083 | 5893 | 239 | 333 | 351 | 507 | 0.354 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3468 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
16520015 |  |  | 1 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3075.2 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 3075 | 3875 | 4083 | 5893 | 264 | 333 | 351 | 507 | 0.42877 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3844 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
13520016 |  |  | 1 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2166.48 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2166 | 5667 | 5971 | 8618 | 186 | 487 | 514 | 741 | 0.59615 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3186 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
15020016 |  |  | 1 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2581 | 5667 | 5971 | 8618 | 222 | 487 | 514 | 741 | 0.84084 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3796 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
16520016 |  |  | 1 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2955.28 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2955 | 5667 | 5971 | 8618 | 254 | 487 | 514 | 741 | 1.0927 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 802.9 | 845.45 | 1221 | 0.95 | 0.95 | 0.95 | 803 | 845 | 1221 | 345 | 363 | 525 | 1.9842 | 2.1911 | 4.5036 | 4 | 13.2 | 14.7 | 23.5 |  | 4346 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 803 | 845 | 1221 |  | 0 | 0 | 0 | 1
13520020 |  |  | 1 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3296 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3296 | 5215 | 5684 | 7393 | 283 | 448 | 489 | 636 | 0.37293 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4120 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
15020020 |  |  | 1 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3880 | 5215 | 5684 | 7393 | 334 | 448 | 489 | 636 | 0.51461 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4850 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
16520020 |  |  | 1 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4296 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 4296 | 5215 | 5684 | 7393 | 369 | 448 | 489 | 636 | 0.62468 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 5370 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
13520021 |  |  | 1 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3382.4 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3382 | 7299 | 7690 | 11098 | 291 | 628 | 661 | 954 | 0.58901 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 4228 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
15020021 |  |  | 1 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4131 | 7299 | 7690 | 11098 | 355 | 628 | 661 | 954 | 0.8636 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 5164 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
16520021 |  |  | 1 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4848 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4848 | 7299 | 7690 | 11098 | 417 | 628 | 661 | 954 | 1.1778 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 875.7193 | 922.7225 | 1331.6485 | 0.85 | 0.85 | 0.85 | 876 | 923 | 1332 | 377 | 397 | 573 | 0.96968 | 1.0713 | 2.1757 | 5.3 | 13.2 | 14.7 | 23.5 |  | 6060 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 876 | 923 | 1332 |  | 0 | 0 | 0 | 1
13522010 |  |  | 1 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1658.413 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1658 | 3561 | 3891 | 5129 | 143 | 306 | 335 | 441 | 0.16124 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 1842.6812 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
15022010 |  |  | 1 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1987.0174 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1987 | 3561 | 3891 | 5129 | 171 | 306 | 335 | 441 | 0.22475 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2207.7971 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
16522010 |  |  | 1 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2236.3565 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2236 | 3561 | 3891 | 5129 | 192 | 306 | 335 | 441 | 0.27878 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2484.8406 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
13522011 |  |  | 1 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1668.7594 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1669 | 4831 | 5279 | 6959 | 144 | 415 | 454 | 598 | 0.29407 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2454.058 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
15022011 |  |  | 1 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1933.9003 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1934 | 4831 | 5279 | 6959 | 166 | 415 | 454 | 598 | 0.38207 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2843.971 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
16522011 |  |  | 1 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2153.1067 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2153 | 4831 | 5279 | 6959 | 185 | 415 | 454 | 598 | 0.46654 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 748.4982 | 817.8264 | 1078.1245 | 0.95 | 0.95 | 0.95 | 748 | 818 | 1078 | 322 | 352 | 464 | 1.2999 | 1.5334 | 2.5617 | 2.9 | 13.4 | 14.8 | 24 |  | 3166.3333 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 748 | 818 | 1078 |  | 0 | 0 | 0 | 1
13522015 |  |  | 1 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2413.3565 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2413 | 4303 | 4482 | 6541 | 208 | 370 | 385 | 563 | 0.27905 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3016.6957 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
15022015 |  |  | 1 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2847.0493 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2847 | 4303 | 4482 | 6541 | 245 | 370 | 385 | 563 | 0.38205 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3558.8116 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
16522015 |  |  | 1 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3155.5594 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3156 | 4303 | 4482 | 6541 | 271 | 370 | 385 | 563 | 0.46373 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3944.4493 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
13522016 |  |  | 1 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2222.8806 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2223 | 6292 | 6554 | 9565 | 191 | 541 | 564 | 823 | 0.64166 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 3268.942 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
15022016 |  |  | 1 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2648.5014 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2649 | 6292 | 6554 | 9565 | 228 | 541 | 564 | 823 | 0.90457 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 3894.8551 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
16522016 |  |  | 1 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3032.258 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3032 | 6292 | 6554 | 9565 | 261 | 541 | 564 | 823 | 1.176 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 891.1063 | 928.2293 | 1354.6625 | 0.95 | 0.95 | 0.95 | 891 | 928 | 1355 | 383 | 399 | 583 | 2.4791 | 2.6848 | 5.6233 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4459.2029 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 891 | 928 | 1355 |  | 0 | 0 | 0 | 1
13522020 |  |  | 1 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3381.9826 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3382 | 5697 | 6224 | 8205 | 291 | 490 | 535 | 706 | 0.40243 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 4227.4783 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
15022020 |  |  | 1 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3981.2174 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3981 | 5697 | 6224 | 8205 | 342 | 490 | 535 | 706 | 0.55039 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 4976.5217 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
16522020 |  |  | 1 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4408.0696 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4408 | 5697 | 6224 | 8205 | 379 | 490 | 535 | 706 | 0.67182 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 5510.087 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
13522021 |  |  | 1 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3470.9101 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3471 | 8103 | 8440 | 12318 | 299 | 697 | 726 | 1059 | 0.63888 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 4338.6377 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
15022021 |  |  | 1 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4239.1072 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4239 | 8103 | 8440 | 12318 | 365 | 697 | 726 | 1059 | 0.93691 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 5298.8841 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
16522021 |  |  | 1 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4974.4696 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4974 | 8103 | 8440 | 12318 | 428 | 697 | 726 | 1059 | 1.2724 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 972.2277 | 1012.7301 | 1477.9835 | 0.85 | 0.85 | 0.85 | 972 | 1013 | 1478 | 418 | 436 | 636 | 1.2159 | 1.3186 | 2.7293 | 5.9 | 15.5 | 16.8 | 27.5 |  | 6218.087 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 972 | 1013 | 1478 |  | 0 | 0 | 0 | 1
13524010 |  |  | 1 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1939.5 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1940 | 3860 | 4229 | 5637 | 167 | 332 | 364 | 485 | 0.22624 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2155 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
15024010 |  |  | 1 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2324 | 3860 | 4229 | 5637 | 200 | 332 | 364 | 485 | 0.31605 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2582 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
16524010 |  |  | 1 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2615.4 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2615 | 3860 | 4229 | 5637 | 225 | 332 | 364 | 485 | 0.39329 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2906 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
13524011 |  |  | 1 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1951.6 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1952 | 5238 | 5738 | 7648 | 168 | 450 | 493 | 658 | 0.41313 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 2870 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
15024011 |  |  | 1 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2262 | 5238 | 5738 | 7648 | 195 | 450 | 493 | 658 | 0.54331 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 3326 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
16524011 |  |  | 1 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2518.04 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2518 | 5238 | 5738 | 7648 | 217 | 450 | 493 | 658 | 0.66141 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 811.225 | 888.925 | 1184.925 | 0.95 | 0.95 | 0.95 | 811 | 889 | 1185 | 349 | 382 | 510 | 1.5893 | 1.8785 | 3.2091 | 3.2 | 14.8 | 16.6 | 28 |  | 3703 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 811 | 889 | 1185 |  | 0 | 0 | 0 | 1
13524015 |  |  | 1 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2822.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2822 | 4730 | 4902 | 7188 | 243 | 407 | 422 | 618 | 0.38667 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 3528 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
15024015 |  |  | 1 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3330 | 4730 | 4902 | 7188 | 286 | 407 | 422 | 618 | 0.52835 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4162 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
16524015 |  |  | 1 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3690.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3690 | 4730 | 4902 | 7188 | 317 | 407 | 422 | 618 | 0.64365 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4613 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
13524016 |  |  | 1 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2599.64 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2600 | 6916 | 7168 | 10512 | 224 | 595 | 616 | 904 | 0.89243 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 3823 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
15024016 |  |  | 1 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3097 | 6916 | 7168 | 10512 | 266 | 595 | 616 | 904 | 1.2449 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 4555 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
16524016 |  |  | 1 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3546.2 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3546 | 6916 | 7168 | 10512 | 305 | 595 | 616 | 904 | 1.6231 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 979.575 | 1015.65 | 1489.25 | 0.95 | 0.95 | 0.95 | 980 | 1016 | 1489 | 421 | 437 | 640 | 3.0352 | 3.2635 | 6.8589 | 4.8 | 16.4 | 17.7 | 29.7 |  | 5215 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 980 | 1016 | 1489 |  | 0 | 0 | 0 | 1
13524020 |  |  | 1 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3955.2 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3955 | 6176 | 6766 | 9018 | 340 | 531 | 582 | 776 | 0.5556 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 4944 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
15024020 |  |  | 1 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4656 | 6176 | 6766 | 9018 | 400 | 531 | 582 | 776 | 0.76111 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 5820 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
16524020 |  |  | 1 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5155.2 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 5155 | 6176 | 6766 | 9018 | 443 | 531 | 582 | 776 | 0.92768 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 6444 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
13524021 |  |  | 1 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4059.2 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4059 | 8907 | 9231 | 13538 | 349 | 766 | 794 | 1164 | 0.88353 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 5074 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
15024021 |  |  | 1 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4958 | 8907 | 9231 | 13538 | 426 | 766 | 794 | 1164 | 1.2947 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 6197 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
16524021 |  |  | 1 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5817.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 5818 | 8907 | 9231 | 13538 | 500 | 766 | 794 | 1164 | 1.7608 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1068.7506 | 1107.6299 | 1624.3185 | 0.85 | 0.85 | 0.85 | 1069 | 1108 | 1624 | 460 | 476 | 698 | 1.5003 | 1.6021 | 3.3449 | 6.4 | 16.4 | 17.7 | 29.7 |  | 7272 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1624 |  | 0 | 0 | 0 | 1
13526010 |  |  | 1 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2008.3753 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2008 | 4178 | 4608 | 6144 | 173 | 359 | 396 | 528 | 0.25338 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2231.5281 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
15026010 |  |  | 1 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2407.0146 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2407 | 4178 | 4608 | 6144 | 207 | 359 | 396 | 528 | 0.35307 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2674.4607 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
16526010 |  |  | 1 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2708.9899 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2709 | 4178 | 4608 | 6144 | 233 | 359 | 396 | 528 | 0.43955 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 3009.9888 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
13526011 |  |  | 1 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2021.4413 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2021 | 5669 | 6253 | 8337 | 174 | 488 | 538 | 717 | 0.4646 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 2972.7079 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
15026011 |  |  | 1 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2342.5542 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2343 | 5669 | 6253 | 8337 | 202 | 488 | 538 | 717 | 0.61076 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3444.9326 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
16526011 |  |  | 1 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2607.5326 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2608 | 5669 | 6253 | 8337 | 224 | 488 | 538 | 717 | 0.73836 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 878.2979 | 968.7109 | 1291.6145 | 0.95 | 0.95 | 0.95 | 878 | 969 | 1292 | 378 | 417 | 556 | 1.9342 | 2.3186 | 3.9468 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3834.6067 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 878 | 969 | 1292 |  | 0 | 0 | 0 | 1
13526015 |  |  | 1 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2922.8225 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 2923 | 4942 | 5122 | 7511 | 251 | 425 | 440 | 646 | 0.42261 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 3653.5281 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
15026015 |  |  | 1 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3447.5955 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3448 | 4942 | 5122 | 7511 | 297 | 425 | 440 | 646 | 0.58297 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4309.4944 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
16526015 |  |  | 1 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3821.8247 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3822 | 4942 | 5122 | 7511 | 329 | 425 | 440 | 646 | 0.70908 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4777.2809 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
13526016 |  |  | 1 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2692.036 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2692 | 7342 | 7610 | 11159 | 232 | 631 | 654 | 960 | 0.97472 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 3958.8764 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
15026016 |  |  | 1 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3207.5065 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3208 | 7342 | 7610 | 11159 | 276 | 631 | 654 | 960 | 1.3636 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 4716.9213 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
16526016 |  |  | 1 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3672.2751 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3672 | 7342 | 7610 | 11159 | 316 | 631 | 654 | 960 | 1.7719 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 988.7048 | 1024.6723 | 1502.6625 | 0.95 | 0.95 | 0.95 | 989 | 1025 | 1503 | 425 | 441 | 646 | 3.147 | 3.381 | 7.0991 | 5.2 | 16.4 | 17.7 | 29.7 |  | 5400.4045 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 989 | 1025 | 1503 |  | 0 | 0 | 0 | 1
13526020 |  |  | 1 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4095.9281 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4096 | 6445 | 7108 | 9477 | 352 | 554 | 611 | 815 | 0.60632 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 5119.9101 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
15026020 |  |  | 1 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4821.6629 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4822 | 6445 | 7108 | 9477 | 415 | 554 | 611 | 815 | 0.8335 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 6027.0787 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
16526020 |  |  | 1 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5338.6247 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 5339 | 6445 | 7108 | 9477 | 459 | 554 | 611 | 815 | 1.0129 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 6673.2809 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
13526021 |  |  | 1 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4203.1551 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4203 | 9235 | 9571 | 14035 | 361 | 794 | 823 | 1207 | 0.96798 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 5253.9438 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
15026021 |  |  | 1 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5134.1124 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5134 | 9235 | 9571 | 14035 | 442 | 794 | 823 | 1207 | 1.4256 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 6417.6404 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
16526021 |  |  | 1 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6024.5933 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 6025 | 9235 | 9571 | 14035 | 518 | 794 | 823 | 1207 | 1.9318 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1079.9492 | 1119.2361 | 1641.3385 | 0.85 | 0.85 | 0.85 | 1080 | 1119 | 1641 | 464 | 481 | 706 | 1.5645 | 1.6761 | 3.4996 | 6.9 | 16.4 | 17.7 | 29.7 |  | 7530.7416 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1080 | 1119 | 1641 |  | 0 | 0 | 0 | 1
13528010 |  |  | 1 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2262.6 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2263 | 4331 | 4782 | 6370 | 195 | 372 | 411 | 548 | 0.33074 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 2514 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
15028010 |  |  | 1 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2712 | 4331 | 4782 | 6370 | 233 | 372 | 411 | 548 | 0.45943 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3013 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
16528010 |  |  | 1 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3051.9 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 3052 | 4331 | 4782 | 6370 | 262 | 372 | 411 | 548 | 0.57068 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3391 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
13528011 |  |  | 1 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2277.32 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2277 | 5977 | 6599 | 8790 | 196 | 514 | 568 | 756 | 0.60736 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3349 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
15028011 |  |  | 1 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2639 | 5977 | 6599 | 8790 | 227 | 514 | 568 | 756 | 0.79462 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3881 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
16528011 |  |  | 1 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2937.6 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2938 | 5977 | 6599 | 8790 | 253 | 514 | 568 | 756 | 0.96929 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 884.3 | 976.8 | 1300.55 | 0.95 | 0.95 | 0.95 | 884 | 977 | 1301 | 380 | 420 | 559 | 2.046 | 2.46 | 4.1678 | 3.7 | 16.2 | 18.6 | 31.4 |  | 4320 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 884 | 977 | 1301 |  | 0 | 0 | 0 | 1
13528015 |  |  | 1 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3292.8 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3293 | 5584 | 5709 | 8484 | 283 | 480 | 491 | 730 | 0.54531 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4116 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
15028015 |  |  | 1 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3884 | 5584 | 5709 | 8484 | 334 | 480 | 491 | 730 | 0.74818 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4855 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
16528015 |  |  | 1 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4305.6 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 4306 | 5584 | 5709 | 8484 | 370 | 480 | 491 | 730 | 0.90984 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 5382 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
13528016 |  |  | 1 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3032.8 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3033 | 8166 | 8348 | 12406 | 261 | 702 | 718 | 1067 | 1.2479 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 4460 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
15028016 |  |  | 1 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3614 | 8166 | 8348 | 12406 | 311 | 702 | 718 | 1067 | 1.7504 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 5314 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
16528016 |  |  | 1 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4137.12 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 4137 | 8166 | 8348 | 12406 | 356 | 702 | 718 | 1067 | 2.273 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1156.25 | 1182.15 | 1757.5 | 0.95 | 0.95 | 0.95 | 1156 | 1182 | 1758 | 497 | 508 | 756 | 4.337 | 4.525 | 9.7908 | 5.6 | 19.3 | 20.4 | 34.5 |  | 6084 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1156 | 1182 | 1758 |  | 0 | 0 | 0 | 1
13528020 |  |  | 1 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4614.4 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 4614 | 7237 | 7990 | 10642 | 397 | 622 | 687 | 915 | 0.77994 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 5768 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
15028020 |  |  | 1 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 5432 | 7237 | 7990 | 10642 | 467 | 622 | 687 | 915 | 1.0671 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 6790 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
16528020 |  |  | 1 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6014.4 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 6014 | 7237 | 7990 | 10642 | 517 | 622 | 687 | 915 | 1.2989 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 7518 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
13528021 |  |  | 1 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4735.2 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 4735 | 10516 | 10751 | 15977 | 407 | 904 | 925 | 1374 | 1.2486 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1364.0875 | 1394.6194 | 2072.42 | 0.85 | 0.85 | 0.85 | 1364 | 1395 | 2072 | 587 | 600 | 891 | 2.5138 | 2.6215 | 5.5955 | 7.5 | 19.3 | 20.4 | 34.5 |  | 5919 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1364 | 1395 | 2072 |  | 0 | 0 | 0 | 1
15028021 |  |  | 1 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 5784 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 5784 | 10516 | 10751 | 15977 | 497 | 904 | 925 | 1374 | 1.8285 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1364.0875 | 1394.6194 | 2072.42 | 0.85 | 0.85 | 0.85 | 1364 | 1395 | 2072 | 587 | 600 | 891 | 2.5138 | 2.6215 | 5.5955 | 7.5 | 19.3 | 20.4 | 34.5 |  | 7230 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1364 | 1395 | 2072 |  | 0 | 0 | 0 | 1
16528021 |  |  | 1 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 6787.2 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 6787 | 10516 | 10751 | 15977 | 584 | 904 | 925 | 1374 | 2.4893 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 8484 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
2205010 |  |  | 2 | 20 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 255.6 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 256 | 649 | 695 | 812 | 22 | 56 | 60 | 70 | 0.0023325 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 284 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
2206010 |  |  | 2 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 306.9 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 307 | 842 | 901 | 1066 | 26 | 72 | 77 | 92 | 0.0034436 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 341 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
2206015 |  |  | 2 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 498.4 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 498 | 957 | 1028 | 1360 | 43 | 82 | 88 | 117 | 0.0095875 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 623 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
2206020 |  |  | 2 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 668.8 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 669 | 1347 | 1442 | 1706 | 58 | 116 | 124 | 147 | 0.013656 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 836 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
2207010 |  |  | 2 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 358.2 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 358 | 1030 | 1104 | 1320 | 31 | 89 | 95 | 114 | 0.0051304 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 398 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
2207015 |  |  | 2 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 581.6 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 582 | 1071 | 1150 | 1521 | 50 | 92 | 99 | 131 | 0.013243 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 727 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
2207020 |  |  | 2 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 780.8 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 781 | 1510 | 1619 | 1936 | 67 | 130 | 139 | 166 | 0.018507 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 976 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
2208010 |  |  | 2 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 408.6 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 409 | 1214 | 1304 | 1574 | 35 | 104 | 112 | 135 | 0.0068432 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 454 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
2208015 |  |  | 2 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 664 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 664 | 1395 | 1496 | 2008 | 57 | 120 | 129 | 173 | 0.017556 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 830 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
2208020 |  |  | 2 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 892 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 892 | 1943 | 2086 | 2518 | 77 | 167 | 179 | 217 | 0.024789 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1115 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
2209010 |  |  | 2 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 459.9 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 460 | 1396 | 1501 | 1828 | 40 | 120 | 129 | 157 | 0.009295 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 511 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
2209015 |  |  | 2 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 747.2 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 747 | 1598 | 1712 | 2331 | 64 | 137 | 147 | 200 | 0.02255 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 934 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
2209020 |  |  | 2 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1004 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1004 | 2233 | 2402 | 2925 | 86 | 192 | 207 | 252 | 0.031349 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1255 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
22010010 |  |  | 2 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 511.2 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 511 | 1574 | 1696 | 2082 | 44 | 135 | 146 | 179 | 0.011692 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 568 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
22010015 |  |  | 2 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 830.4 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 830 | 1799 | 1926 | 2655 | 71 | 155 | 166 | 228 | 0.028248 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1038 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
22010020 |  |  | 2 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1115.2 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1115 | 2519 | 2714 | 3331 | 96 | 217 | 233 | 286 | 0.039559 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 1394 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
22011010 |  |  | 2 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 562.5 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 563 | 1766 | 1903 | 2336 | 48 | 152 | 164 | 201 | 0.014427 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 625 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
22011015 |  |  | 2 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 913.6 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 914 | 1908 | 2043 | 2817 | 79 | 164 | 176 | 242 | 0.035539 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1142 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
22011020 |  |  | 2 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1226 | 2693 | 2901 | 3561 | 105 | 232 | 249 | 306 | 0.047916 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 1533 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
22012010 |  |  | 2 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 613.8 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 614 | 1925 | 2080 | 2590 | 53 | 166 | 179 | 223 | 0.018157 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 682 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
22012015 |  |  | 2 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 996.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 997 | 2217 | 2374 | 3303 | 86 | 191 | 204 | 284 | 0.0428 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1246 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
22012020 |  |  | 2 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1338.4 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 1338 | 3080 | 3327 | 4143 | 115 | 265 | 286 | 356 | 0.058145 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 1673 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
22014010 |  |  | 2 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 715.5 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 716 | 2268 | 2456 | 3098 | 62 | 195 | 211 | 266 | 0.026399 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 795 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
22014015 |  |  | 2 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1162.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1162 | 2629 | 2815 | 3950 | 100 | 226 | 242 | 340 | 0.059645 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 1453 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
22014020 |  |  | 2 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1561.6 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1562 | 3628 | 3929 | 4956 | 134 | 312 | 338 | 426 | 0.080718 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 1952 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
22016010 |  |  | 2 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 818.1 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 818 | 2604 | 2827 | 3605 | 70 | 224 | 243 | 310 | 0.035612 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 909 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
22016015 |  |  | 2 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1328.8 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1329 | 3021 | 3226 | 4598 | 114 | 260 | 277 | 395 | 0.079722 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 1661 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
22016020 |  |  | 2 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1784 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1784 | 4166 | 4522 | 5768 | 153 | 358 | 389 | 496 | 0.10744 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 2230 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
22018010 |  |  | 2 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 919.8 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 920 | 2971 | 3225 | 4113 | 79 | 256 | 277 | 354 | 0.04768 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1022 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
22018015 |  |  | 2 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1494.4 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 1494 | 3233 | 3452 | 4921 | 128 | 278 | 297 | 423 | 0.10318 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 1868 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
22018020 |  |  | 2 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2007 | 4498 | 4883 | 6228 | 173 | 387 | 420 | 536 | 0.14003 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 2509 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
22020010 |  |  | 2 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1022.4 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1022 | 3260 | 3553 | 4621 | 88 | 280 | 306 | 397 | 0.061952 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1136 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
22020015 |  |  | 2 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1660.8 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1661 | 3875 | 4083 | 5893 | 143 | 333 | 351 | 507 | 0.13193 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 2076 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
22020020 |  |  | 2 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2230.4 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2230 | 5215 | 5684 | 7393 | 192 | 448 | 489 | 636 | 0.17571 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 2788 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
22022010 |  |  | 2 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1125 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1125 | 3561 | 3891 | 5129 | 97 | 306 | 335 | 441 | 0.078563 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 1250 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
22022015 |  |  | 2 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1827.2 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1827 | 4303 | 4482 | 6541 | 157 | 370 | 385 | 563 | 0.16281 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 2284 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
22022020 |  |  | 2 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2453.6 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2454 | 5697 | 6224 | 8205 | 211 | 490 | 535 | 706 | 0.216 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 3067 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
22024010 |  |  | 2 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1226.7 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1227 | 3860 | 4229 | 5637 | 106 | 332 | 364 | 485 | 0.097646 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 1363 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
22024015 |  |  | 2 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 1992.8 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1993 | 4730 | 4902 | 7188 | 171 | 407 | 422 | 618 | 0.1975 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 2491 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
22024020 |  |  | 2 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2676.8 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2677 | 6176 | 6766 | 9018 | 230 | 531 | 582 | 776 | 0.26102 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 3346 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
22026010 |  |  | 2 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1329.3 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1329 | 4178 | 4608 | 6144 | 114 | 359 | 396 | 528 | 0.11743 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 1477 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
22026015 |  |  | 2 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2159.2 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.08 | 1.08 | 1.08 | 2159 | 5669 | 6253 | 8337 | 186 | 488 | 538 | 717 | 0.23858 | 1.5103 | 1.8217 | 3.1664 | 0.0002083 | 1.724 | 2 | 0.00046183 | 949.5112 | 1047.255 | 1396.34 | 1.01 | 1.01 | 1.01 | 950 | 1047 | 1396 | 409 | 450 | 600 | 1.0761 | 1.2926 | 2.2469 | 2.6 | 16.2 | 18.6 | 31.4 |  | 2699 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
22026020 |  |  | 2 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2899.2 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2899 | 6445 | 7108 | 9477 | 249 | 554 | 611 | 815 | 0.31093 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 3624 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
22028010 |  |  | 2 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1431.9 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 1432 | 4331 | 4782 | 6370 | 123 | 372 | 411 | 548 | 0.14162 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 1591 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
22028015 |  |  | 2 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2324.8 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 2325 | 5584 | 5709 | 8484 | 200 | 480 | 491 | 730 | 0.28153 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 2906 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
22028020 |  |  | 2 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3122.4 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 3122 | 7237 | 7990 | 10642 | 268 | 622 | 687 | 915 | 0.36586 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 3903 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
2355010 |  |  | 2 | 35 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 353.7 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 354 | 649 | 695 | 812 | 30 | 56 | 60 | 70 | 0.0042507 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 393 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
2355011 |  |  | 2 | 35 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 373.32 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 373 | 881 | 943 | 1102 | 32 | 76 | 81 | 95 | 0.0080238 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 549 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1
2356010 |  |  | 2 | 35 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 423.9 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 424 | 842 | 901 | 1066 | 36 | 72 | 77 | 92 | 0.0064417 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 471 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
2356011 |  |  | 2 | 35 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 448.12 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 448 | 1142 | 1223 | 1447 | 39 | 98 | 105 | 124 | 0.012641 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 659 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1
2356015 |  |  | 2 | 35 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 632 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 632 | 957 | 1028 | 1360 | 54 | 82 | 88 | 117 | 0.015003 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 790 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
2356016 |  |  | 2 | 35 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 663 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 663 | 1400 | 1503 | 1989 | 57 | 120 | 129 | 171 | 0.04831 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 975 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1
2356020 |  |  | 2 | 35 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 864.8 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 865 | 1347 | 1442 | 1706 | 74 | 116 | 124 | 147 | 0.022097 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1081 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
2356021 |  |  | 2 | 35 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 997.6 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 998 | 1803 | 1935 | 2561 | 86 | 155 | 166 | 220 | 0.042158 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1247 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1
2357010 |  |  | 2 | 35 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 495 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 495 | 1030 | 1104 | 1320 | 43 | 89 | 95 | 114 | 0.0096037 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 550 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
2357011 |  |  | 2 | 35 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 522.92 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 523 | 1397 | 1498 | 1791 | 45 | 120 | 129 | 154 | 0.017775 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 769 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1
2357015 |  |  | 2 | 35 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 737.6 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 738 | 1071 | 1150 | 1521 | 63 | 92 | 99 | 131 | 0.020835 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 922 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
2357016 |  |  | 2 | 35 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 773.84 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 774 | 1628 | 1747 | 2313 | 67 | 140 | 150 | 199 | 0.067658 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1138 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1
2357020 |  |  | 2 | 35 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1008.8 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1009 | 1510 | 1619 | 1936 | 87 | 130 | 139 | 166 | 0.030975 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1261 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
2357021 |  |  | 2 | 35 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1164 | 1978 | 2123 | 2810 | 100 | 170 | 183 | 242 | 0.058119 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1455 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1
2358010 |  |  | 2 | 35 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 565.2 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 565 | 1214 | 1304 | 1574 | 49 | 104 | 112 | 135 | 0.013005 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 628 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
2358011 |  |  | 2 | 35 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 597.04 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 597 | 1648 | 1770 | 2136 | 51 | 142 | 152 | 184 | 0.023989 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 878 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
2358015 |  |  | 2 | 35 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 843.2 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 843 | 1395 | 1496 | 2008 | 72 | 120 | 129 | 173 | 0.027727 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1054 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
2358016 |  |  | 2 | 35 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 884 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 884 | 2040 | 2188 | 2936 | 76 | 175 | 188 | 252 | 0.088202 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1300 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
2358020 |  |  | 2 | 35 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1152.8 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1153 | 1943 | 2086 | 2518 | 99 | 167 | 179 | 217 | 0.040654 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1441 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
2358021 |  |  | 2 | 35 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1329.6 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1330 | 2628 | 2818 | 3781 | 114 | 226 | 242 | 325 | 0.076913 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 1662 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1
2359010 |  |  | 2 | 35 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 636.3 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 636 | 1396 | 1501 | 1828 | 55 | 120 | 129 | 157 | 0.017032 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 707 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
2359011 |  |  | 2 | 35 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 671.84 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 672 | 1894 | 2037 | 2480 | 58 | 163 | 175 | 213 | 0.032402 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 988 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1
2359015 |  |  | 2 | 35 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 948 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 948 | 1598 | 1712 | 2331 | 82 | 137 | 147 | 200 | 0.036582 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1185 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
2359016 |  |  | 2 | 35 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 994.84 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 995 | 2337 | 2503 | 3409 | 86 | 201 | 215 | 293 | 0.1143 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1463 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
2359020 |  |  | 2 | 35 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1296.8 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1297 | 2233 | 2402 | 2925 | 112 | 192 | 207 | 252 | 0.052682 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1621 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
2359021 |  |  | 2 | 35 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1496 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1496 | 3009 | 3224 | 4391 | 129 | 259 | 277 | 378 | 0.10015 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 1870 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
23510010 |  |  | 2 | 35 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 706.5 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 707 | 1574 | 1696 | 2082 | 61 | 135 | 146 | 179 | 0.021718 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 785 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
23510011 |  |  | 2 | 35 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 746.64 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 747 | 2136 | 2301 | 2825 | 64 | 184 | 198 | 243 | 0.041142 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1098 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
23510015 |  |  | 2 | 35 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1053.6 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1054 | 1799 | 1926 | 2655 | 91 | 155 | 166 | 228 | 0.045812 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1317 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
23510016 |  |  | 2 | 35 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1105 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1105 | 2630 | 2817 | 3883 | 95 | 226 | 242 | 334 | 0.14114 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1625 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
23510020 |  |  | 2 | 35 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1440.8 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1441 | 2519 | 2714 | 3331 | 124 | 217 | 233 | 286 | 0.065364 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 1801 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
23510021 |  |  | 2 | 35 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1662.4 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 1662 | 3388 | 3627 | 5000 | 143 | 291 | 312 | 430 | 0.12507 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2078 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
23511010 |  |  | 2 | 35 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 777.6 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 778 | 1766 | 1903 | 2336 | 67 | 152 | 164 | 201 | 0.027098 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 864 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
23511011 |  |  | 2 | 35 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 821.44 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 821 | 2397 | 2582 | 3169 | 71 | 206 | 222 | 273 | 0.05256 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1208 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
23511015 |  |  | 2 | 35 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1159.2 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1159 | 1908 | 2043 | 2817 | 100 | 164 | 176 | 242 | 0.056209 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1449 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
23511016 |  |  | 2 | 35 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1215.84 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1216 | 2850 | 3051 | 4207 | 105 | 245 | 262 | 362 | 0.17431 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 1788 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
23511020 |  |  | 2 | 35 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1584.8 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1585 | 2693 | 2901 | 3561 | 136 | 232 | 249 | 306 | 0.079545 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 1981 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
23511021 |  |  | 2 | 35 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1828.8 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 1829 | 3556 | 3808 | 5249 | 157 | 306 | 327 | 451 | 0.1531 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2286 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
23512010 |  |  | 2 | 35 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 847.8 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 848 | 1925 | 2080 | 2590 | 73 | 166 | 179 | 223 | 0.033204 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 942 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
23512011 |  |  | 2 | 35 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 896.24 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 896 | 2612 | 2822 | 3514 | 77 | 225 | 243 | 302 | 0.064125 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1318 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
23512015 |  |  | 2 | 35 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1264 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1264 | 2217 | 2374 | 3303 | 109 | 191 | 204 | 284 | 0.067805 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1580 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
23512016 |  |  | 2 | 35 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1326 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1326 | 3242 | 3472 | 4830 | 114 | 279 | 299 | 415 | 0.20771 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 1950 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
23512020 |  |  | 2 | 35 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1728.8 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 1729 | 3080 | 3327 | 4143 | 149 | 265 | 286 | 356 | 0.09652 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2161 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
23512021 |  |  | 2 | 35 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1995.2 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 1995 | 4175 | 4471 | 6220 | 172 | 359 | 385 | 535 | 0.18642 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 2494 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
23514010 |  |  | 2 | 35 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 989.1 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 989 | 2268 | 2456 | 3098 | 85 | 195 | 211 | 266 | 0.047722 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1099 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
23514011 |  |  | 2 | 35 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1045.16 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1045 | 3077 | 3333 | 4203 | 90 | 265 | 287 | 361 | 0.093537 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1537 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
23514015 |  |  | 2 | 35 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1475.2 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1475 | 2629 | 2815 | 3950 | 127 | 226 | 242 | 340 | 0.09472 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 1844 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
23514016 |  |  | 2 | 35 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1547 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1547 | 3844 | 4117 | 5777 | 133 | 331 | 354 | 497 | 0.28849 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2275 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
23514020 |  |  | 2 | 35 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1936.8 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1937 | 3628 | 3929 | 4956 | 167 | 312 | 338 | 426 | 0.12404 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 2421 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
23514021 |  |  | 2 | 35 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2327.2 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2327 | 4951 | 5302 | 7440 | 200 | 426 | 456 | 640 | 0.25915 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 2909 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
23516010 |  |  | 2 | 35 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1130.4 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1130 | 2604 | 2827 | 3605 | 97 | 224 | 243 | 310 | 0.065521 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1256 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
23516011 |  |  | 2 | 35 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1194.76 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1195 | 3533 | 3835 | 4892 | 103 | 304 | 330 | 421 | 0.12995 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 1757 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
23516015 |  |  | 2 | 35 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1685.6 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1686 | 3021 | 3226 | 4598 | 145 | 260 | 277 | 395 | 0.1268 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2107 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
23516016 |  |  | 2 | 35 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1768 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1768 | 4418 | 4717 | 6724 | 152 | 380 | 406 | 578 | 0.384 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 2600 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
23516020 |  |  | 2 | 35 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2305.6 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 2306 | 4166 | 4522 | 5768 | 198 | 358 | 389 | 496 | 0.1775 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 2882 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
23516021 |  |  | 2 | 35 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2660 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 2660 | 5690 | 6075 | 8659 | 229 | 489 | 522 | 745 | 0.34853 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 3325 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
23518010 |  |  | 2 | 35 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1271.7 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1272 | 2971 | 3225 | 4113 | 109 | 256 | 277 | 354 | 0.086839 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1413 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
23518011 |  |  | 2 | 35 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1343.68 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1344 | 4031 | 4376 | 5581 | 116 | 347 | 376 | 480 | 0.17391 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 1976 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
23518015 |  |  | 2 | 35 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1896.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 1897 | 3233 | 3452 | 4921 | 163 | 278 | 297 | 423 | 0.16429 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 2371 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
23518016 |  |  | 2 | 35 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1989 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 1989 | 4843 | 5171 | 7371 | 171 | 417 | 445 | 634 | 0.49478 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 2925 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
23518020 |  |  | 2 | 35 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2593.6 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2594 | 4498 | 4883 | 6228 | 223 | 387 | 420 | 536 | 0.22932 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 3242 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
23518021 |  |  | 2 | 35 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2992 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2992 | 6017 | 6424 | 9157 | 257 | 517 | 552 | 788 | 0.44974 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 3740 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
23520010 |  |  | 2 | 35 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1413 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1413 | 3260 | 3553 | 4621 | 122 | 280 | 306 | 397 | 0.11363 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1570 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
23520011 |  |  | 2 | 35 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1493.28 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1493 | 4423 | 4821 | 6270 | 128 | 380 | 415 | 539 | 0.22274 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2196 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
23520015 |  |  | 2 | 35 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2107.2 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2107 | 3875 | 4083 | 5893 | 181 | 333 | 351 | 507 | 0.2074 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 2634 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
23520016 |  |  | 2 | 35 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2210 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2210 | 5667 | 5971 | 8618 | 190 | 487 | 514 | 741 | 0.62131 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3250 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
23520020 |  |  | 2 | 35 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2881.6 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2882 | 5215 | 5684 | 7393 | 248 | 448 | 489 | 636 | 0.28861 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 3602 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
23520021 |  |  | 2 | 35 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3324.8 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3325 | 7299 | 7690 | 11098 | 286 | 628 | 661 | 954 | 0.5697 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 4156 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
23522010 |  |  | 2 | 35 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1554.3 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1554 | 3561 | 3891 | 5129 | 134 | 306 | 335 | 441 | 0.14292 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 1727 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
23522011 |  |  | 2 | 35 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1642.88 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1643 | 4831 | 5279 | 6959 | 141 | 415 | 454 | 598 | 0.2829 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2416 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
23522015 |  |  | 2 | 35 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2317.6 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2318 | 4303 | 4482 | 6541 | 199 | 370 | 385 | 563 | 0.25636 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 2897 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
23522016 |  |  | 2 | 35 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2431 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2431 | 6292 | 6554 | 9565 | 209 | 541 | 564 | 823 | 0.76407 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 3575 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
23522020 |  |  | 2 | 35 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3169.6 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3170 | 5697 | 6224 | 8205 | 273 | 490 | 535 | 706 | 0.3556 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 3962 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
23522021 |  |  | 2 | 35 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3657.6 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3658 | 8103 | 8440 | 12318 | 315 | 697 | 726 | 1059 | 0.70607 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 4572 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
23524010 |  |  | 2 | 35 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1695.6 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1696 | 3860 | 4229 | 5637 | 146 | 332 | 364 | 485 | 0.17641 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 1884 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
23524011 |  |  | 2 | 35 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1791.8 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1792 | 5238 | 5738 | 7648 | 154 | 450 | 493 | 658 | 0.35214 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 2635 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
23524015 |  |  | 2 | 35 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2528.8 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2529 | 4730 | 4902 | 7188 | 217 | 407 | 422 | 618 | 0.31137 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 3161 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
23524016 |  |  | 2 | 35 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2652 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2652 | 6916 | 7168 | 10512 | 228 | 595 | 616 | 904 | 0.92354 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 3900 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
23524020 |  |  | 2 | 35 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3457.6 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3458 | 6176 | 6766 | 9018 | 297 | 531 | 582 | 776 | 0.42772 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 4322 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
23524021 |  |  | 2 | 35 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3989.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3990 | 8907 | 9231 | 13538 | 343 | 766 | 794 | 1164 | 0.85467 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 4987 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
23526010 |  |  | 2 | 35 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1836.9 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1837 | 4178 | 4608 | 6144 | 158 | 359 | 396 | 528 | 0.21431 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2041 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
23526011 |  |  | 2 | 35 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1941.4 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1941 | 5669 | 6253 | 8337 | 167 | 488 | 538 | 717 | 0.43094 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 2855 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
23526015 |  |  | 2 | 35 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2739.2 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 2739 | 4942 | 5122 | 7511 | 236 | 425 | 440 | 646 | 0.37569 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 3424 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
23526016 |  |  | 2 | 35 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2893.4 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2893 | 7342 | 7610 | 11159 | 249 | 631 | 654 | 960 | 1.1175 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 4255 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
23526020 |  |  | 2 | 35 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3746.4 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3746 | 6445 | 7108 | 9477 | 322 | 554 | 611 | 815 | 0.5105 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 4683 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
23526021 |  |  | 2 | 35 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4322.4 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4322 | 9235 | 9571 | 14035 | 372 | 794 | 823 | 1207 | 1.0251 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 5403 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
23528010 |  |  | 2 | 35 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1978.2 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 1978 | 4331 | 4782 | 6370 | 170 | 372 | 411 | 548 | 0.25683 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 2198 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
23528011 |  |  | 2 | 35 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2090.32 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2090 | 5977 | 6599 | 8790 | 180 | 514 | 568 | 756 | 0.51978 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3074 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
23528015 |  |  | 2 | 35 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2950.4 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 2950 | 5584 | 5709 | 8484 | 254 | 480 | 491 | 730 | 0.44374 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 3688 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
23528016 |  |  | 2 | 35 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3094 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3094 | 8166 | 8348 | 12406 | 266 | 702 | 718 | 1067 | 1.2944 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 4550 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
23528020 |  |  | 2 | 35 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4034.4 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 4034 | 7237 | 7990 | 10642 | 347 | 622 | 687 | 915 | 0.60163 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 5043 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
23528021 |  |  | 2 | 35 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.9 | 4654.4 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 4654 | 10516 | 10751 | 15977 | 400 | 904 | 925 | 1374 | 1.2079 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 5818 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
2505010 |  |  | 2 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 434 | 649 | 695 | 812 | 37 | 56 | 60 | 70 | 0.0063825 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 482 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
2505011 |  |  | 2 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 445.4 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 445 | 881 | 943 | 1102 | 38 | 76 | 81 | 95 | 0.011173 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 655 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1
2506010 |  |  | 2 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 520 | 842 | 901 | 1066 | 45 | 72 | 77 | 92 | 0.0099056 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 578 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
2506011 |  |  | 2 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 533.8 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 534 | 1142 | 1223 | 1447 | 46 | 98 | 105 | 124 | 0.017343 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 785 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1
2506015 |  |  | 2 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 736 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 736 | 957 | 1028 | 1360 | 63 | 82 | 88 | 117 | 0.020318 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 920 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
2506016 |  |  | 2 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 796.28 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 796 | 1400 | 1503 | 1989 | 68 | 120 | 129 | 171 | 0.068487 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1171 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1
2506020 |  |  | 2 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1017.6 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1018 | 1347 | 1442 | 1706 | 88 | 116 | 124 | 147 | 0.031124 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1272 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
2506021 |  |  | 2 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1230.4 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1230 | 1803 | 1935 | 2561 | 106 | 155 | 166 | 220 | 0.063626 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1538 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1
2507010 |  |  | 2 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 607.5 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 608 | 1030 | 1104 | 1320 | 52 | 89 | 95 | 114 | 0.013833 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 675 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
2507011 |  |  | 2 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 622.88 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 623 | 1397 | 1498 | 1791 | 54 | 120 | 129 | 154 | 0.025162 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 916 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1
2507015 |  |  | 2 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 858.4 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 858 | 1071 | 1150 | 1521 | 74 | 92 | 99 | 131 | 0.028573 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1073 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
2507016 |  |  | 2 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 928.88 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 929 | 1628 | 1747 | 2313 | 80 | 140 | 150 | 199 | 0.096025 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1366 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1
2507020 |  |  | 2 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1187.2 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1187 | 1510 | 1619 | 1936 | 102 | 130 | 139 | 166 | 0.042396 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1484 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
2507021 |  |  | 2 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1436 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1436 | 1978 | 2123 | 2810 | 123 | 170 | 183 | 242 | 0.087274 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1795 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1
2508010 |  |  | 2 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693.9 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 694 | 1214 | 1304 | 1574 | 60 | 104 | 112 | 135 | 0.019158 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 771 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
2508011 |  |  | 2 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 711.96 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 712 | 1648 | 1770 | 2136 | 61 | 142 | 152 | 184 | 0.033698 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1047 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
2508015 |  |  | 2 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 981 | 1395 | 1496 | 2008 | 84 | 120 | 129 | 173 | 0.037498 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
2508016 |  |  | 2 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1061.48 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1061 | 2040 | 2188 | 2936 | 91 | 175 | 188 | 252 | 0.1258 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1561 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
2508020 |  |  | 2 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1356.8 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1357 | 1943 | 2086 | 2518 | 117 | 167 | 179 | 217 | 0.056497 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
2508021 |  |  | 2 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1640.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1641 | 2628 | 2818 | 3781 | 141 | 226 | 242 | 325 | 0.11666 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 2051 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1
2509010 |  |  | 2 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 781.2 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 781 | 1396 | 1501 | 1828 | 67 | 120 | 129 | 157 | 0.024809 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 868 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
2509011 |  |  | 2 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 801.04 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 801 | 1894 | 2037 | 2480 | 69 | 163 | 175 | 213 | 0.044999 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1178 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1
2509015 |  |  | 2 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1104 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1104 | 1598 | 1712 | 2331 | 95 | 137 | 147 | 200 | 0.048773 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1380 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
2509016 |  |  | 2 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1194.08 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1194 | 2337 | 2503 | 3409 | 103 | 201 | 215 | 293 | 0.16303 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1756 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
2509020 |  |  | 2 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1526.4 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1526 | 2233 | 2402 | 2925 | 131 | 192 | 207 | 252 | 0.071701 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1908 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
2509021 |  |  | 2 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1846.4 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1846 | 3009 | 3224 | 4391 | 159 | 259 | 277 | 378 | 0.15074 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 2308 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
25010010 |  |  | 2 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 867.6 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 868 | 1574 | 1696 | 2082 | 75 | 135 | 146 | 179 | 0.032159 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 964 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
25010011 |  |  | 2 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 890.12 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 890 | 2136 | 2301 | 2825 | 77 | 184 | 198 | 243 | 0.0583 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1309 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
25010015 |  |  | 2 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1226.4 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1226 | 1799 | 1926 | 2655 | 105 | 155 | 166 | 228 | 0.060563 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1533 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
25010016 |  |  | 2 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1326.68 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1327 | 2630 | 2817 | 3883 | 114 | 226 | 242 | 334 | 0.20197 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1951 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
25010020 |  |  | 2 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1696 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1696 | 2519 | 2714 | 3331 | 146 | 217 | 233 | 286 | 0.090085 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2120 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
25010021 |  |  | 2 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2051.2 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2051 | 3388 | 3627 | 5000 | 176 | 291 | 312 | 430 | 0.18758 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2564 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
25011010 |  |  | 2 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 954 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 954 | 1766 | 1903 | 2336 | 82 | 152 | 164 | 201 | 0.039734 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1060 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
25011011 |  |  | 2 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 979.2 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 979 | 2397 | 2582 | 3169 | 84 | 206 | 222 | 273 | 0.072092 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1440 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
25011015 |  |  | 2 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1348.8 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1349 | 1908 | 2043 | 2817 | 116 | 164 | 176 | 242 | 0.075043 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1686 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
25011016 |  |  | 2 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1459.28 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1459 | 2850 | 3051 | 4207 | 125 | 245 | 262 | 362 | 0.24545 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2146 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
25011020 |  |  | 2 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1865.6 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1866 | 2693 | 2901 | 3561 | 160 | 232 | 249 | 306 | 0.10941 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2332 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
25011021 |  |  | 2 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2256 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2256 | 3556 | 3808 | 5249 | 194 | 306 | 327 | 451 | 0.23124 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2820 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
25012010 |  |  | 2 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1041.3 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1041 | 1925 | 2080 | 2590 | 90 | 166 | 179 | 223 | 0.049317 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1157 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
25012011 |  |  | 2 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1068.28 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1068 | 2612 | 2822 | 3514 | 92 | 225 | 243 | 302 | 0.089517 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1571 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
25012015 |  |  | 2 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1472 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1472 | 2217 | 2374 | 3303 | 127 | 191 | 204 | 284 | 0.091261 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1840 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
25012016 |  |  | 2 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1591.88 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1592 | 3242 | 3472 | 4830 | 137 | 279 | 299 | 415 | 0.29781 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2341 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
25012020 |  |  | 2 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2035 | 3080 | 3327 | 4143 | 175 | 265 | 286 | 356 | 0.13226 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2544 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
25012021 |  |  | 2 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2461.6 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2462 | 4175 | 4471 | 6220 | 212 | 359 | 385 | 535 | 0.28 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3077 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
25014010 |  |  | 2 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1215 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1215 | 2268 | 2456 | 3098 | 104 | 195 | 211 | 266 | 0.069746 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1350 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
25014011 |  |  | 2 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1246.44 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1246 | 3077 | 3333 | 4203 | 107 | 265 | 287 | 361 | 0.12917 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1833 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
25014015 |  |  | 2 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1716.8 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1717 | 2629 | 2815 | 3950 | 148 | 226 | 242 | 340 | 0.12741 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2146 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
25014016 |  |  | 2 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1857.08 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1857 | 3844 | 4117 | 5777 | 160 | 331 | 354 | 497 | 0.41412 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2731 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
25014020 |  |  | 2 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2374 | 3628 | 3929 | 4956 | 204 | 312 | 338 | 426 | 0.18338 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 2968 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
25014021 |  |  | 2 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2872 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2872 | 4951 | 5302 | 7440 | 247 | 426 | 456 | 640 | 0.39025 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 3590 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
25016010 |  |  | 2 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1387.8 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1388 | 2604 | 2827 | 3605 | 119 | 224 | 243 | 310 | 0.096097 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1542 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
25016011 |  |  | 2 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1423.92 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1424 | 3533 | 3835 | 4892 | 122 | 304 | 330 | 421 | 0.17798 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 2094 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
25016015 |  |  | 2 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1962.4 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1962 | 3021 | 3226 | 4598 | 169 | 260 | 277 | 395 | 0.17047 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2453 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
25016016 |  |  | 2 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2122.96 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2123 | 4418 | 4717 | 6724 | 183 | 380 | 406 | 578 | 0.55164 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3122 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
25016020 |  |  | 2 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 2714 | 4166 | 4522 | 5768 | 233 | 358 | 389 | 496 | 0.24378 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3392 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
25016021 |  |  | 2 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3281.6 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3282 | 5690 | 6075 | 8659 | 282 | 489 | 522 | 745 | 0.52134 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4102 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
25018010 |  |  | 2 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1561.5 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1562 | 2971 | 3225 | 4113 | 134 | 256 | 277 | 354 | 0.12769 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1735 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
25018011 |  |  | 2 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1602.08 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1602 | 4031 | 4376 | 5581 | 138 | 347 | 376 | 480 | 0.23988 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2356 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
25018015 |  |  | 2 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2207.2 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2207 | 3233 | 3452 | 4921 | 190 | 278 | 297 | 423 | 0.22074 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 2759 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
25018016 |  |  | 2 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.16 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2388 | 4843 | 5171 | 7371 | 205 | 417 | 445 | 634 | 0.70438 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3512 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
25018020 |  |  | 2 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3053 | 4498 | 4883 | 6228 | 263 | 387 | 420 | 536 | 0.31611 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 3816 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
25018021 |  |  | 2 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3692 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3692 | 6017 | 6424 | 9157 | 318 | 517 | 552 | 788 | 0.67829 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 4615 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
25020010 |  |  | 2 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1735.2 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1735 | 3260 | 3553 | 4621 | 149 | 280 | 306 | 397 | 0.16487 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1928 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
25020011 |  |  | 2 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1780.24 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1780 | 4423 | 4821 | 6270 | 153 | 380 | 415 | 539 | 0.30962 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2618 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
25020015 |  |  | 2 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2452.8 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2453 | 3875 | 4083 | 5893 | 211 | 333 | 351 | 507 | 0.27852 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3066 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
25020016 |  |  | 2 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2653.36 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2653 | 5667 | 5971 | 8618 | 228 | 487 | 514 | 741 | 0.8856 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3902 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
25020020 |  |  | 2 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3392 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3392 | 5215 | 5684 | 7393 | 292 | 448 | 489 | 636 | 0.39632 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4240 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
25020021 |  |  | 2 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4102.4 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4102 | 7299 | 7690 | 11098 | 353 | 628 | 661 | 954 | 0.85425 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 5128 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
25022010 |  |  | 2 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1908.9 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1909 | 3561 | 3891 | 5129 | 164 | 306 | 335 | 441 | 0.20795 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2121 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
25022011 |  |  | 2 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1958.4 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1958 | 4831 | 5279 | 6959 | 168 | 415 | 454 | 598 | 0.39059 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2880 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
25022015 |  |  | 2 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2698.4 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2698 | 4303 | 4482 | 6541 | 232 | 370 | 385 | 563 | 0.34408 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3373 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
25022016 |  |  | 2 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2918.56 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2919 | 6292 | 6554 | 9565 | 251 | 541 | 564 | 823 | 1.0901 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4292 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
25022020 |  |  | 2 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3731 | 5697 | 6224 | 8205 | 321 | 490 | 535 | 706 | 0.48674 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 4664 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
25022021 |  |  | 2 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4512.8 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4513 | 8103 | 8440 | 12318 | 388 | 697 | 726 | 1059 | 1.0536 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 5641 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
25024010 |  |  | 2 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2082.6 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2083 | 3860 | 4229 | 5637 | 179 | 332 | 364 | 485 | 0.25728 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2314 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
25024011 |  |  | 2 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2136.56 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2137 | 5238 | 5738 | 7648 | 184 | 450 | 493 | 658 | 0.4883 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 3142 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
25024015 |  |  | 2 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2943.2 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2943 | 4730 | 4902 | 7188 | 253 | 407 | 422 | 618 | 0.41772 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 3679 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
25024016 |  |  | 2 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3183.76 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3184 | 6916 | 7168 | 10512 | 274 | 595 | 616 | 904 | 1.3185 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 4682 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
25024020 |  |  | 2 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4070 | 6176 | 6766 | 9018 | 350 | 531 | 582 | 776 | 0.58766 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 5088 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
25024021 |  |  | 2 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4923.2 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4923 | 8907 | 9231 | 13538 | 423 | 766 | 794 | 1164 | 1.2773 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 6154 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
25026010 |  |  | 2 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2255.4 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2255 | 4178 | 4608 | 6144 | 194 | 359 | 396 | 528 | 0.31315 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2506 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
25026011 |  |  | 2 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2314.04 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2314 | 5669 | 6253 | 8337 | 199 | 488 | 538 | 717 | 0.59423 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3403 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
25026015 |  |  | 2 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3188.8 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3189 | 4942 | 5122 | 7511 | 274 | 425 | 440 | 646 | 0.49969 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 3986 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
25026016 |  |  | 2 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3449.64 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3450 | 7342 | 7610 | 11159 | 297 | 631 | 654 | 960 | 1.5715 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 5073 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
25026020 |  |  | 2 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4410 | 6445 | 7108 | 9477 | 379 | 554 | 611 | 815 | 0.69938 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 5512 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
25026021 |  |  | 2 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5332.8 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5333 | 9235 | 9571 | 14035 | 459 | 794 | 823 | 1207 | 1.5324 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 6666 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
25028010 |  |  | 2 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2429.1 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2429 | 4331 | 4782 | 6370 | 209 | 372 | 411 | 548 | 0.37587 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 2699 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
25028011 |  |  | 2 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2492.2 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2492 | 5977 | 6599 | 8790 | 214 | 514 | 568 | 756 | 0.71329 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3665 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
25028015 |  |  | 2 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3433.6 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3434 | 5584 | 5709 | 8484 | 295 | 480 | 491 | 730 | 0.59027 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4292 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
25028016 |  |  | 2 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3714.84 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3715 | 8166 | 8348 | 12406 | 319 | 702 | 718 | 1067 | 1.8385 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 5463 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
25028020 |  |  | 2 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 4749 | 7237 | 7990 | 10642 | 408 | 622 | 687 | 915 | 0.82218 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 5936 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
25028021 |  |  | 2 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5743.2 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 5743 | 10516 | 10751 | 15977 | 494 | 904 | 925 | 1374 | 1.8074 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 7179 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
2655010 |  |  | 2 | 65 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 504.9 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 505 | 649 | 695 | 812 | 43 | 56 | 60 | 70 | 0.0085435 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 561 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
2655011 |  |  | 2 | 65 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 504.56 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 505 | 881 | 943 | 1102 | 43 | 76 | 81 | 95 | 0.01418 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 136.4943 | 146.0591 | 170.792 | 0.95 | 0.95 | 0.95 | 136 | 146 | 171 | 58 | 63 | 74 | 0.025275 | 0.029658 | 0.040497 | 0.7 | 3.6 | 4.1 | 5.1 |  | 742 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 136 | 146 | 171 |  | 0 | 0 | 0 | 1
2656010 |  |  | 2 | 65 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 605.7 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 606 | 842 | 901 | 1066 | 52 | 72 | 77 | 92 | 0.013096 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 673 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
2656011 |  |  | 2 | 65 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 605.2 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 605 | 1142 | 1223 | 1447 | 52 | 98 | 105 | 124 | 0.02194 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 176.675 | 189.625 | 223.85 | 0.95 | 0.95 | 0.95 | 177 | 190 | 224 | 76 | 82 | 96 | 0.045491 | 0.052655 | 0.071338 | 0.8 | 4.8 | 5.4 | 6.8 |  | 890 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 177 | 190 | 224 |  | 0 | 0 | 0 | 1
2656015 |  |  | 2 | 65 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 823.2 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 823 | 957 | 1028 | 1360 | 71 | 82 | 88 | 117 | 0.025709 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1029 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
2656016 |  |  | 2 | 65 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 908.48 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 908 | 1400 | 1503 | 1989 | 78 | 120 | 129 | 171 | 0.089849 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 197.95 | 212.75 | 282.125 | 0.95 | 0.95 | 0.95 | 198 | 213 | 282 | 85 | 92 | 121 | 0.10651 | 0.12458 | 0.21435 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1336 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 198 | 213 | 282 |  | 0 | 0 | 0 | 1
2656020 |  |  | 2 | 65 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1148 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1148 | 1347 | 1442 | 1706 | 99 | 116 | 124 | 147 | 0.039288 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1435 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
2656021 |  |  | 2 | 65 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1442.4 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1442 | 1803 | 1935 | 2561 | 124 | 155 | 166 | 220 | 0.086661 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 216.2921 | 232.1848 | 307.3035 | 0.85 | 0.85 | 0.85 | 216 | 232 | 307 | 93 | 100 | 132 | 0.049177 | 0.056729 | 0.098024 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1803 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 216 | 232 | 307 |  | 0 | 0 | 0 | 1
2657010 |  |  | 2 | 65 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 706.5 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 707 | 1030 | 1104 | 1320 | 61 | 89 | 95 | 114 | 0.018801 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 785 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
2657011 |  |  | 2 | 65 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 705.84 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 706 | 1397 | 1498 | 1791 | 61 | 120 | 129 | 154 | 0.031753 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 216.4625 | 232.1327 | 277.537 | 0.95 | 0.95 | 0.95 | 216 | 232 | 278 | 93 | 100 | 120 | 0.071145 | 0.081763 | 0.116 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1038 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 216 | 232 | 278 |  | 0 | 0 | 0 | 1
2657015 |  |  | 2 | 65 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 960.8 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 961 | 1071 | 1150 | 1521 | 83 | 92 | 99 | 131 | 0.035798 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1201 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
2657016 |  |  | 2 | 65 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1060.12 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1060 | 1628 | 1747 | 2313 | 91 | 140 | 150 | 199 | 0.12386 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.1279 | 218.0533 | 288.6 | 0.95 | 0.95 | 0.95 | 203 | 218 | 289 | 87 | 94 | 124 | 0.11333 | 0.13205 | 0.22833 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1559 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 203 | 218 | 289 |  | 0 | 0 | 0 | 1
2657020 |  |  | 2 | 65 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1339.2 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1339 | 1510 | 1619 | 1936 | 115 | 130 | 139 | 166 | 0.053725 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1674 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
2657021 |  |  | 2 | 65 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1683.2 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1683 | 1978 | 2123 | 2810 | 145 | 170 | 183 | 242 | 0.1206 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.2818 | 238.6146 | 315.8135 | 0.85 | 0.85 | 0.85 | 222 | 239 | 316 | 95 | 103 | 136 | 0.052552 | 0.061591 | 0.10633 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2104 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 222 | 239 | 316 |  | 0 | 0 | 0 | 1
2658010 |  |  | 2 | 65 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 807.3 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 807 | 1214 | 1304 | 1574 | 69 | 104 | 112 | 135 | 0.025037 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 897 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
2658011 |  |  | 2 | 65 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 806.48 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 806 | 1648 | 1770 | 2136 | 69 | 142 | 152 | 184 | 0.042591 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 255.3 | 273.8 | 331.15 | 0.95 | 0.95 | 0.95 | 255 | 274 | 331 | 110 | 118 | 142 | 0.10357 | 0.11843 | 0.16872 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1186 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 255 | 274 | 331 |  | 0 | 0 | 0 | 1
2658015 |  |  | 2 | 65 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1097.6 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1098 | 1395 | 1496 | 2008 | 94 | 120 | 129 | 173 | 0.046744 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1372 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
2658016 |  |  | 2 | 65 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1211.76 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1212 | 2040 | 2188 | 2936 | 104 | 175 | 188 | 252 | 0.16371 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 288.6 | 309.875 | 416.25 | 0.95 | 0.95 | 0.95 | 289 | 310 | 416 | 124 | 133 | 179 | 0.23165 | 0.26601 | 0.47834 | 1.6 | 6 | 6.7 | 9 |  | 1782 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 289 | 310 | 416 |  | 0 | 0 | 0 | 1
2658020 |  |  | 2 | 65 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1530.4 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1530 | 1943 | 2086 | 2518 | 132 | 167 | 179 | 217 | 0.071661 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1913 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
2658021 |  |  | 2 | 65 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1923.2 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1923 | 2628 | 2818 | 3781 | 165 | 226 | 242 | 325 | 0.15879 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 315.2976 | 338.1017 | 453.6385 | 0.85 | 0.85 | 0.85 | 315 | 338 | 454 | 135 | 145 | 195 | 0.10712 | 0.12323 | 0.22041 | 2.1 | 6 | 6.7 | 9 |  | 2404 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 315 | 338 | 454 |  | 0 | 0 | 0 | 1
2659010 |  |  | 2 | 65 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 908.1 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 908 | 1396 | 1501 | 1828 | 78 | 120 | 129 | 157 | 0.033161 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1009 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
2659011 |  |  | 2 | 65 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 907.8 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 908 | 1894 | 2037 | 2480 | 78 | 163 | 175 | 213 | 0.056758 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 293.3758 | 315.5893 | 384.282 | 0.95 | 0.95 | 0.95 | 293 | 316 | 384 | 126 | 136 | 165 | 0.14109 | 0.16316 | 0.23581 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1335 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 293 | 316 | 384 |  | 0 | 0 | 0 | 1
2659015 |  |  | 2 | 65 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1235.2 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1235 | 1598 | 1712 | 2331 | 106 | 137 | 147 | 200 | 0.060427 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1544 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
2659016 |  |  | 2 | 65 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1362.72 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1363 | 2337 | 2503 | 3409 | 117 | 201 | 215 | 293 | 0.20955 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 330.9459 | 354.5558 | 482.85 | 0.95 | 0.95 | 0.95 | 331 | 355 | 483 | 142 | 153 | 208 | 0.30693 | 0.35557 | 0.65174 | 1.8 | 7 | 7.7 | 10.7 |  | 2004 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 331 | 355 | 483 |  | 0 | 0 | 0 | 1
2659020 |  |  | 2 | 65 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1721.6 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1722 | 2233 | 2402 | 2925 | 148 | 192 | 207 | 252 | 0.091161 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2152 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
2659021 |  |  | 2 | 65 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2164 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2164 | 3009 | 3224 | 4391 | 186 | 259 | 277 | 378 | 0.20492 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 361.0734 | 386.8326 | 526.806 | 0.85 | 0.85 | 0.85 | 361 | 387 | 527 | 155 | 166 | 227 | 0.14341 | 0.16401 | 0.30277 | 2.4 | 7 | 7.7 | 10.7 |  | 2705 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 361 | 387 | 527 |  | 0 | 0 | 0 | 1
26510010 |  |  | 2 | 65 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1008.9 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1009 | 1574 | 1696 | 2082 | 87 | 135 | 146 | 179 | 0.042655 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1121 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
26510011 |  |  | 2 | 65 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1008.44 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1008 | 2136 | 2301 | 2825 | 87 | 184 | 198 | 243 | 0.073411 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 331.15 | 356.125 | 437.525 | 0.95 | 0.95 | 0.95 | 331 | 356 | 438 | 142 | 153 | 188 | 0.18556 | 0.21378 | 0.31619 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1483 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 331 | 356 | 438 |  | 0 | 0 | 0 | 1
26510015 |  |  | 2 | 65 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1372 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1372 | 1799 | 1926 | 2655 | 118 | 155 | 166 | 228 | 0.076061 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1715 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
26510016 |  |  | 2 | 65 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1514.36 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1514 | 2630 | 2817 | 3883 | 130 | 226 | 242 | 334 | 0.2615 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 372.775 | 398.675 | 550.375 | 0.95 | 0.95 | 0.95 | 373 | 399 | 550 | 160 | 172 | 237 | 0.39352 | 0.45375 | 0.85347 | 2 | 7 | 7.7 | 10.7 |  | 2227 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 373 | 399 | 550 |  | 0 | 0 | 0 | 1
26510020 |  |  | 2 | 65 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1912.8 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1913 | 2519 | 2714 | 3331 | 165 | 217 | 233 | 286 | 0.11457 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2391 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
26510021 |  |  | 2 | 65 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2404 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2404 | 3388 | 3627 | 5000 | 207 | 291 | 312 | 430 | 0.25756 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 406.4601 | 435.2289 | 599.9735 | 0.85 | 0.85 | 0.85 | 406 | 435 | 600 | 175 | 187 | 258 | 0.18551 | 0.21117 | 0.39627 | 2.7 | 7 | 7.7 | 10.7 |  | 3005 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 406 | 435 | 600 |  | 0 | 0 | 0 | 1
26511010 |  |  | 2 | 65 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.7 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1110 | 1766 | 1903 | 2336 | 95 | 152 | 164 | 201 | 0.052533 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1233 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
26511011 |  |  | 2 | 65 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1109.08 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1109 | 2397 | 2582 | 3169 | 95 | 206 | 222 | 273 | 0.090878 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 371.314 | 400.0249 | 491.027 | 0.95 | 0.95 | 0.95 | 371 | 400 | 491 | 160 | 172 | 211 | 0.24309 | 0.27875 | 0.41057 | 1.5 | 8.4 | 9.3 | 14 |  | 1631 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 371 | 400 | 491 |  | 0 | 0 | 0 | 1
26511015 |  |  | 2 | 65 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1509.6 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1510 | 1908 | 2043 | 2817 | 130 | 164 | 176 | 242 | 0.093701 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1887 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
26511016 |  |  | 2 | 65 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1666 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1666 | 2850 | 3051 | 4207 | 143 | 245 | 262 | 362 | 0.31969 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 377.2455 | 403.9466 | 556.85 | 0.95 | 0.95 | 0.95 | 377 | 404 | 557 | 162 | 174 | 240 | 0.40852 | 0.47015 | 0.88527 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2450 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 377 | 404 | 557 |  | 0 | 0 | 0 | 1
26511020 |  |  | 2 | 65 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2104 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2104 | 2693 | 2901 | 3561 | 181 | 232 | 249 | 306 | 0.13937 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2630 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
26511021 |  |  | 2 | 65 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2644.8 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2645 | 3556 | 3808 | 5249 | 227 | 306 | 327 | 451 | 0.31417 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 412.2253 | 441.4022 | 608.4835 | 0.85 | 0.85 | 0.85 | 412 | 441 | 608 | 177 | 190 | 261 | 0.19338 | 0.22204 | 0.41259 | 2.9 | 7.9 | 8.8 | 12.5 |  | 3306 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 412 | 441 | 608 |  | 0 | 0 | 0 | 1
26512010 |  |  | 2 | 65 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1210.5 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1211 | 1925 | 2080 | 2590 | 104 | 166 | 179 | 223 | 0.06484 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1345 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
26512011 |  |  | 2 | 65 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1210.4 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1210 | 2612 | 2822 | 3514 | 104 | 225 | 243 | 302 | 0.11268 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 404.225 | 437.525 | 544.825 | 0.95 | 0.95 | 0.95 | 404 | 438 | 545 | 174 | 188 | 234 | 0.29689 | 0.34359 | 0.51965 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1780 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 404 | 438 | 545 |  | 0 | 0 | 0 | 1
26512015 |  |  | 2 | 65 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1646.4 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1646 | 2217 | 2374 | 3303 | 142 | 191 | 204 | 284 | 0.1134 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2058 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
26512016 |  |  | 2 | 65 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1816.96 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1817 | 3242 | 3472 | 4830 | 156 | 279 | 299 | 415 | 0.38424 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 458.8 | 492.1 | 684.5 | 0.95 | 0.95 | 0.95 | 459 | 492 | 685 | 197 | 212 | 295 | 0.60758 | 0.70182 | 1.344 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2672 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 459 | 492 | 685 |  | 0 | 0 | 0 | 1
26512020 |  |  | 2 | 65 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2295.2 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2295 | 3080 | 3327 | 4143 | 197 | 265 | 286 | 356 | 0.16682 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2869 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
26512021 |  |  | 2 | 65 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2884.8 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2885 | 4175 | 4471 | 6220 | 248 | 359 | 385 | 535 | 0.38004 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 500.9437 | 536.44 | 746.3085 | 0.85 | 0.85 | 0.85 | 501 | 536 | 746 | 215 | 230 | 321 | 0.28777 | 0.32815 | 0.62857 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3606 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 501 | 536 | 746 |  | 0 | 0 | 0 | 1
26514010 |  |  | 2 | 65 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1412.1 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1412 | 2268 | 2456 | 3098 | 121 | 195 | 211 | 266 | 0.092769 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1569 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
26514011 |  |  | 2 | 65 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1411.68 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1412 | 3077 | 3333 | 4203 | 121 | 265 | 287 | 361 | 0.16252 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 476.375 | 516.15 | 651.2 | 0.95 | 0.95 | 0.95 | 476 | 516 | 651 | 205 | 222 | 280 | 0.43647 | 0.50695 | 0.78463 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2076 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 476 | 516 | 651 |  | 0 | 0 | 0 | 1
26514015 |  |  | 2 | 65 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1920.8 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1921 | 2629 | 2815 | 3950 | 165 | 226 | 242 | 340 | 0.15733 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2401 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
26514016 |  |  | 2 | 65 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2120.24 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2120 | 3844 | 4117 | 5777 | 182 | 331 | 354 | 497 | 0.53291 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 544.825 | 582.75 | 818.625 | 0.95 | 0.95 | 0.95 | 545 | 583 | 819 | 234 | 251 | 352 | 0.87198 | 1.0005 | 1.9431 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3118 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 545 | 583 | 819 |  | 0 | 0 | 0 | 1
26514020 |  |  | 2 | 65 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2677.6 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2678 | 3628 | 3929 | 4956 | 230 | 312 | 338 | 426 | 0.23187 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3347 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
26514021 |  |  | 2 | 65 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3365.6 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3366 | 4951 | 5302 | 7440 | 289 | 426 | 456 | 640 | 0.52941 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 594.0588 | 636.1954 | 892.6435 | 0.85 | 0.85 | 0.85 | 594 | 636 | 893 | 255 | 273 | 384 | 0.41516 | 0.47396 | 0.9201 | 3.7 | 9.6 | 10.5 | 16.1 |  | 4207 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 594 | 636 | 893 |  | 0 | 0 | 0 | 1
26516010 |  |  | 2 | 65 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1614.6 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1615 | 2604 | 2827 | 3605 | 139 | 224 | 243 | 310 | 0.12863 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1794 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
26516011 |  |  | 2 | 65 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1613.64 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1614 | 3533 | 3835 | 4892 | 139 | 304 | 330 | 421 | 0.22688 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 547.6 | 593.85 | 757.575 | 0.95 | 0.95 | 0.95 | 548 | 594 | 758 | 236 | 255 | 326 | 0.60938 | 0.70443 | 1.1164 | 2.1 | 11 | 12.4 | 19.2 |  | 2373 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 548 | 594 | 758 |  | 0 | 0 | 0 | 1
26516015 |  |  | 2 | 65 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2195.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2195 | 3021 | 3226 | 4598 | 189 | 260 | 277 | 395 | 0.21164 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2744 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
26516016 |  |  | 2 | 65 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2422.84 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2423 | 4418 | 4717 | 6724 | 208 | 380 | 406 | 578 | 0.70842 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 625.3 | 667.85 | 952.75 | 0.95 | 0.95 | 0.95 | 625 | 668 | 953 | 269 | 287 | 410 | 1.1714 | 1.3297 | 2.6743 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3563 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 625 | 668 | 953 |  | 0 | 0 | 0 | 1
26516020 |  |  | 2 | 65 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3060.8 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3061 | 4166 | 4522 | 5768 | 263 | 358 | 389 | 496 | 0.30877 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3826 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
26516021 |  |  | 2 | 65 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3846.4 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3846 | 5690 | 6075 | 8659 | 331 | 489 | 522 | 745 | 0.71102 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 682.6809 | 728.8758 | 1038.9785 | 0.85 | 0.85 | 0.85 | 683 | 729 | 1039 | 294 | 313 | 447 | 0.56515 | 0.63802 | 1.2735 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4808 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 683 | 729 | 1039 |  | 0 | 0 | 0 | 1
26518010 |  |  | 2 | 65 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1816.2 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1816 | 2971 | 3225 | 4113 | 156 | 256 | 277 | 354 | 0.16968 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 2018 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
26518011 |  |  | 2 | 65 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1814.92 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1815 | 4031 | 4376 | 5581 | 156 | 347 | 376 | 480 | 0.30111 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 624.4704 | 677.8928 | 864.6345 | 0.95 | 0.95 | 0.95 | 624 | 678 | 865 | 268 | 292 | 372 | 0.82386 | 0.96681 | 1.52 | 2.4 | 12.2 | 13.7 | 22 |  | 2669 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 624 | 678 | 865 |  | 0 | 0 | 0 | 1
26518015 |  |  | 2 | 65 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2469.6 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2470 | 3233 | 3452 | 4921 | 212 | 278 | 297 | 423 | 0.27269 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3087 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
26518016 |  |  | 2 | 65 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2726.12 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2726 | 4843 | 5171 | 7371 | 234 | 417 | 445 | 634 | 0.91166 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 634.8357 | 677.7931 | 966.1625 | 0.95 | 0.95 | 0.95 | 635 | 678 | 966 | 273 | 292 | 415 | 1.2316 | 1.4044 | 2.7919 | 3.6 | 11.5 | 12.8 | 19.6 |  | 4009 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 635 | 678 | 966 |  | 0 | 0 | 0 | 1
26518020 |  |  | 2 | 65 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3443.2 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3443 | 4498 | 4883 | 6228 | 296 | 387 | 420 | 536 | 0.39793 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4304 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
26518021 |  |  | 2 | 65 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4327.2 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4327 | 6017 | 6424 | 9157 | 372 | 517 | 552 | 788 | 0.91835 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 693.8642 | 740.8158 | 1055.9985 | 0.85 | 0.85 | 0.85 | 694 | 741 | 1056 | 298 | 319 | 454 | 0.59835 | 0.68241 | 1.3501 | 4.8 | 11.5 | 12.8 | 19.6 |  | 5409 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 694 | 741 | 1056 |  | 0 | 0 | 0 | 1
26520010 |  |  | 2 | 65 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2017.8 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 2018 | 3260 | 3553 | 4621 | 174 | 280 | 306 | 397 | 0.22016 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2242 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
26520011 |  |  | 2 | 65 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2016.88 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2017 | 4423 | 4821 | 6270 | 173 | 380 | 415 | 539 | 0.38856 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 685.425 | 746.475 | 971.25 | 0.95 | 0.95 | 0.95 | 685 | 746 | 971 | 295 | 321 | 418 | 1.0453 | 1.2231 | 2.0002 | 2.7 | 13.4 | 14.8 | 24 |  | 2966 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 685 | 746 | 971 |  | 0 | 0 | 0 | 1
26520015 |  |  | 2 | 65 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2744 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2744 | 3875 | 4083 | 5893 | 236 | 333 | 351 | 507 | 0.34549 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3430 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
26520016 |  |  | 2 | 65 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3028.72 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3029 | 5667 | 5971 | 8618 | 260 | 487 | 514 | 741 | 1.1435 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 802.9 | 845.45 | 1221 | 0.95 | 0.95 | 0.95 | 803 | 845 | 1221 | 345 | 363 | 525 | 1.9842 | 2.1911 | 4.5036 | 4 | 13.2 | 14.7 | 23.5 |  | 4454 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 803 | 845 | 1221 |  | 0 | 0 | 0 | 1
26520020 |  |  | 2 | 65 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3825.6 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3826 | 5215 | 5684 | 7393 | 329 | 448 | 489 | 636 | 0.49974 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4782 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
26520021 |  |  | 2 | 65 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4808 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4808 | 7299 | 7690 | 11098 | 413 | 628 | 661 | 954 | 1.1561 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 875.7193 | 922.7225 | 1331.6485 | 0.85 | 0.85 | 0.85 | 876 | 923 | 1332 | 377 | 397 | 573 | 0.96968 | 1.0713 | 2.1757 | 5.3 | 13.2 | 14.7 | 23.5 |  | 6010 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 876 | 923 | 1332 |  | 0 | 0 | 0 | 1
26522010 |  |  | 2 | 65 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2219.4 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2219 | 3561 | 3891 | 5129 | 191 | 306 | 335 | 441 | 0.27609 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2466 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
26522011 |  |  | 2 | 65 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2218.84 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2219 | 4831 | 5279 | 6959 | 191 | 415 | 454 | 598 | 0.49483 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 748.4982 | 817.8264 | 1078.1245 | 0.95 | 0.95 | 0.95 | 748 | 818 | 1078 | 322 | 352 | 464 | 1.2999 | 1.5334 | 2.5617 | 2.9 | 13.4 | 14.8 | 24 |  | 3263 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 748 | 818 | 1078 |  | 0 | 0 | 0 | 1
26522015 |  |  | 2 | 65 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3018.4 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3018 | 4303 | 4482 | 6541 | 260 | 370 | 385 | 563 | 0.42824 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3773 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
26522016 |  |  | 2 | 65 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3331.32 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3331 | 6292 | 6554 | 9565 | 286 | 541 | 564 | 823 | 1.4047 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 891.1063 | 928.2293 | 1354.6625 | 0.95 | 0.95 | 0.95 | 891 | 928 | 1355 | 383 | 399 | 583 | 2.4791 | 2.6848 | 5.6233 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4899 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 891 | 928 | 1355 |  | 0 | 0 | 0 | 1
26522020 |  |  | 2 | 65 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4208 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4208 | 5697 | 6224 | 8205 | 362 | 490 | 535 | 706 | 0.61456 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 5260 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
26522021 |  |  | 2 | 65 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5288.8 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 5289 | 8103 | 8440 | 12318 | 455 | 697 | 726 | 1059 | 1.4314 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 972.2277 | 1012.7301 | 1477.9835 | 0.85 | 0.85 | 0.85 | 972 | 1013 | 1478 | 418 | 436 | 636 | 1.2159 | 1.3186 | 2.7293 | 5.9 | 15.5 | 16.8 | 27.5 |  | 6611 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 972 | 1013 | 1478 |  | 0 | 0 | 0 | 1
26524010 |  |  | 2 | 65 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2421 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2421 | 3860 | 4229 | 5637 | 208 | 332 | 364 | 485 | 0.33991 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2690 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
26524011 |  |  | 2 | 65 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2420.12 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2420 | 5238 | 5738 | 7648 | 208 | 450 | 493 | 658 | 0.61181 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 811.225 | 888.925 | 1184.925 | 0.95 | 0.95 | 0.95 | 811 | 889 | 1185 | 349 | 382 | 510 | 1.5893 | 1.8785 | 3.2091 | 3.2 | 14.8 | 16.6 | 28 |  | 3559 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 811 | 889 | 1185 |  | 0 | 0 | 0 | 1
26524015 |  |  | 2 | 65 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3292.8 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3293 | 4730 | 4902 | 7188 | 283 | 407 | 422 | 618 | 0.51777 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4116 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
26524016 |  |  | 2 | 65 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3634.6 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3635 | 6916 | 7168 | 10512 | 313 | 595 | 616 | 904 | 1.7067 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 979.575 | 1015.65 | 1489.25 | 0.95 | 0.95 | 0.95 | 980 | 1016 | 1489 | 421 | 437 | 640 | 3.0352 | 3.2635 | 6.8589 | 4.8 | 16.4 | 17.7 | 29.7 |  | 5345 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 980 | 1016 | 1489 |  | 0 | 0 | 0 | 1
26524020 |  |  | 2 | 65 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4590.4 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4590 | 6176 | 6766 | 9018 | 395 | 531 | 582 | 776 | 0.74278 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 5738 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
26524021 |  |  | 2 | 65 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5769.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 5770 | 8907 | 9231 | 13538 | 496 | 766 | 794 | 1164 | 1.7338 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1068.7506 | 1107.6299 | 1624.3185 | 0.85 | 0.85 | 0.85 | 1069 | 1108 | 1624 | 460 | 476 | 698 | 1.5003 | 1.6021 | 3.3449 | 6.4 | 16.4 | 17.7 | 29.7 |  | 7212 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1624 |  | 0 | 0 | 0 | 1
26526010 |  |  | 2 | 65 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2623.5 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2624 | 4178 | 4608 | 6144 | 226 | 359 | 396 | 528 | 0.4154 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2915 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
26526011 |  |  | 2 | 65 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2622.08 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2622 | 5669 | 6253 | 8337 | 225 | 488 | 538 | 717 | 0.74442 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 878.2979 | 968.7109 | 1291.6145 | 0.95 | 0.95 | 0.95 | 878 | 969 | 1292 | 378 | 417 | 556 | 1.9342 | 2.3186 | 3.9468 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3856 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 878 | 969 | 1292 |  | 0 | 0 | 0 | 1
26526015 |  |  | 2 | 65 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3567.2 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3567 | 4942 | 5122 | 7511 | 307 | 425 | 440 | 646 | 0.6211 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4459 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
26526016 |  |  | 2 | 65 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3937.2 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3937 | 7342 | 7610 | 11159 | 339 | 631 | 654 | 960 | 2.0302 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 988.7048 | 1024.6723 | 1502.6625 | 0.95 | 0.95 | 0.95 | 989 | 1025 | 1503 | 425 | 441 | 646 | 3.147 | 3.381 | 7.0991 | 5.2 | 16.4 | 17.7 | 29.7 |  | 5790 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 989 | 1025 | 1503 |  | 0 | 0 | 0 | 1
26526020 |  |  | 2 | 65 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4973.6 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4974 | 6445 | 7108 | 9477 | 428 | 554 | 611 | 815 | 0.88474 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 6217 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
26526021 |  |  | 2 | 65 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6250.4 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 6250 | 9235 | 9571 | 14035 | 538 | 794 | 823 | 1207 | 2.0773 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1079.9492 | 1119.2361 | 1641.3385 | 0.85 | 0.85 | 0.85 | 1080 | 1119 | 1641 | 464 | 481 | 706 | 1.5645 | 1.6761 | 3.4996 | 6.9 | 16.4 | 17.7 | 29.7 |  | 7813 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1080 | 1119 | 1641 |  | 0 | 0 | 0 | 1
26528010 |  |  | 2 | 65 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2825.1 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2825 | 4331 | 4782 | 6370 | 243 | 372 | 411 | 548 | 0.49652 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3139 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
26528011 |  |  | 2 | 65 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2823.36 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2823 | 5977 | 6599 | 8790 | 243 | 514 | 568 | 756 | 0.90022 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 884.3 | 976.8 | 1300.55 | 0.95 | 0.95 | 0.95 | 884 | 977 | 1301 | 380 | 420 | 559 | 2.046 | 2.46 | 4.1678 | 3.7 | 16.2 | 18.6 | 31.4 |  | 4152 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 884 | 977 | 1301 |  | 0 | 0 | 0 | 1
26528015 |  |  | 2 | 65 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3841.6 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3842 | 5584 | 5709 | 8484 | 330 | 480 | 491 | 730 | 0.73116 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4802 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
26528016 |  |  | 2 | 65 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4240.48 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 4240 | 8166 | 8348 | 12406 | 365 | 702 | 718 | 1067 | 2.3855 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1156.25 | 1182.15 | 1757.5 | 0.95 | 0.95 | 0.95 | 1156 | 1182 | 1758 | 497 | 508 | 756 | 4.337 | 4.525 | 9.7908 | 5.6 | 19.3 | 20.4 | 34.5 |  | 6236 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1156 | 1182 | 1758 |  | 0 | 0 | 0 | 1
26528020 |  |  | 2 | 65 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5356 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 5356 | 7237 | 7990 | 10642 | 461 | 622 | 687 | 915 | 1.0408 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 6695 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
26528021 |  |  | 2 | 65 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6731.2 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 6731 | 10516 | 10751 | 15977 | 579 | 904 | 925 | 1374 | 2.4486 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.1473 | 1193.2712 | 1773.2144 | 0.85 | 0.85 | 0.85 | 1167 | 1193 | 1773 | 502 | 513 | 762 | 1.8638 | 1.9426 | 4.1444 | 7.5 | 19.3 | 20.4 | 34.5 |  | 8414 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1167 | 1193 | 1773 |  | 0 | 0 | 0 | 1
2956010 |  |  | 2 | 95 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 746.6923 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 747 | 842 | 901 | 1066 | 64 | 72 | 77 | 92 | 0.019564 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 838 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
2956011 |  |  | 2 | 95 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 717 | 1142 | 1223 | 1447 | 62 | 98 | 105 | 124 | 0.030755 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 148.025 | 158.875 | 187.55 | 0.95 | 0.95 | 0.95 | 148 | 159 | 188 | 64 | 68 | 81 | 0.032689 | 0.036729 | 0.051426 | 0.8 | 4.8 | 5.4 | 6.8 |  | 1055 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 148 | 159 | 188 |  | 0 | 0 | 0 | 1
2956015 |  |  | 2 | 95 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1210 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
2956016 |  |  | 2 | 95 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1093.44 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1093 | 1400 | 1503 | 1989 | 94 | 120 | 129 | 171 | 0.12999 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 165.85 | 178.25 | 236.375 | 0.95 | 0.95 | 0.95 | 166 | 178 | 236 | 71 | 77 | 101 | 0.074594 | 0.087584 | 0.14986 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1608 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 236 |  | 0 | 0 | 0 | 1
2956020 |  |  | 2 | 95 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1706 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
2956021 |  |  | 2 | 95 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1707.6437 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1708 | 1803 | 1935 | 2561 | 147 | 155 | 166 | 220 | 0.12119 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 181.2177 | 194.5332 | 257.4705 | 0.85 | 0.85 | 0.85 | 181 | 195 | 257 | 78 | 84 | 111 | 0.03479 | 0.04025 | 0.069672 | 1.6 | 4.8 | 5.5 | 7.2 |  | 2290 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 181 | 195 | 257 |  | 0 | 0 | 0 | 1
2957010 |  |  | 2 | 95 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 879.3 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 879 | 1030 | 1104 | 1320 | 76 | 89 | 95 | 114 | 0.028709 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 977 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
2957011 |  |  | 2 | 95 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 837 | 1397 | 1498 | 1791 | 72 | 120 | 129 | 154 | 0.043589 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.3604 | 194.4896 | 232.531 | 0.95 | 0.95 | 0.95 | 181 | 194 | 233 | 78 | 83 | 100 | 0.050801 | 0.057216 | 0.081763 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1231 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 181 | 194 | 233 |  | 0 | 0 | 0 | 1
2957015 |  |  | 2 | 95 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1411 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
2957016 |  |  | 2 | 95 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1275.68 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1276 | 1628 | 1747 | 2313 | 110 | 140 | 150 | 199 | 0.18017 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 170.1882 | 182.6933 | 241.8 | 0.95 | 0.95 | 0.95 | 170 | 183 | 242 | 73 | 79 | 104 | 0.080141 | 0.093669 | 0.16126 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1876 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 170 | 183 | 242 |  | 0 | 0 | 0 | 1
2957020 |  |  | 2 | 95 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1991 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
2957021 |  |  | 2 | 95 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1883 | 1978 | 2123 | 2810 | 162 | 170 | 183 | 242 | 0.14998 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 186.2361 | 199.9203 | 264.6005 | 0.85 | 0.85 | 0.85 | 186 | 200 | 265 | 80 | 86 | 114 | 0.037513 | 0.043229 | 0.075172 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2671 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 186 | 200 | 265 |  | 0 | 0 | 0 | 1
2958010 |  |  | 2 | 95 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 1005.3 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1005 | 1214 | 1304 | 1574 | 86 | 104 | 112 | 135 | 0.038198 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 1117 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
2958011 |  |  | 2 | 95 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 956 | 1648 | 1770 | 2136 | 82 | 142 | 152 | 184 | 0.059152 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 213.9 | 229.4 | 277.45 | 0.95 | 0.95 | 0.95 | 214 | 229 | 277 | 92 | 98 | 119 | 0.073653 | 0.083082 | 0.12035 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1406 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 214 | 229 | 277 |  | 0 | 0 | 0 | 1
2958015 |  |  | 2 | 95 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1290.4 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1290 | 1395 | 1496 | 2008 | 111 | 120 | 129 | 173 | 0.064759 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1613 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
2958016 |  |  | 2 | 95 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1457.92 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1458 | 2040 | 2188 | 2936 | 125 | 175 | 188 | 252 | 0.23535 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 241.8 | 259.625 | 348.75 | 0.95 | 0.95 | 0.95 | 242 | 260 | 349 | 104 | 112 | 150 | 0.16371 | 0.18949 | 0.33734 | 1.6 | 6 | 6.7 | 9 |  | 2144 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 242 | 260 | 349 |  | 0 | 0 | 0 | 1
2958020 |  |  | 2 | 95 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1820 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1820 | 1943 | 2086 | 2518 | 157 | 167 | 179 | 217 | 0.10089 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2275 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
2958021 |  |  | 2 | 95 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2442.4 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 2442 | 2628 | 2818 | 3781 | 210 | 226 | 242 | 325 | 0.25494 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 264.1682 | 283.2744 | 380.0755 | 0.85 | 0.85 | 0.85 | 264 | 283 | 380 | 114 | 122 | 163 | 0.076913 | 0.087842 | 0.15503 | 2.1 | 6 | 6.7 | 9 |  | 3053 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 264 | 283 | 380 |  | 0 | 0 | 0 | 1
2959010 |  |  | 2 | 95 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1130.4 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 1130 | 1396 | 1501 | 1828 | 97 | 120 | 129 | 157 | 0.050305 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1256 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
2959011 |  |  | 2 | 95 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1076 | 1894 | 2037 | 2480 | 93 | 163 | 175 | 213 | 0.079227 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 245.8013 | 264.4127 | 321.966 | 0.95 | 0.95 | 0.95 | 246 | 264 | 322 | 106 | 114 | 138 | 0.10157 | 0.11663 | 0.16776 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1582 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 246 | 264 | 322 |  | 0 | 0 | 0 | 1
2959015 |  |  | 2 | 95 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1451.2 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1451 | 1598 | 1712 | 2331 | 125 | 137 | 147 | 200 | 0.083439 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1814 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
2959016 |  |  | 2 | 95 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1640.16 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1640 | 2337 | 2503 | 3409 | 141 | 201 | 215 | 293 | 0.30268 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 277.279 | 297.0603 | 404.55 | 0.95 | 0.95 | 0.95 | 277 | 297 | 405 | 119 | 128 | 174 | 0.21666 | 0.25014 | 0.45825 | 1.8 | 7 | 7.7 | 10.7 |  | 2412 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 277 | 297 | 405 |  | 0 | 0 | 0 | 1
2959020 |  |  | 2 | 95 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2048 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2048 | 2233 | 2402 | 2925 | 176 | 192 | 207 | 252 | 0.12823 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2560 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
2959021 |  |  | 2 | 95 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2747.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2747 | 3009 | 3224 | 4391 | 236 | 259 | 277 | 378 | 0.32675 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 302.521 | 324.103 | 441.378 | 0.85 | 0.85 | 0.85 | 303 | 324 | 441 | 130 | 139 | 190 | 0.10167 | 0.11588 | 0.21364 | 2.4 | 7 | 7.7 | 10.7 |  | 3434 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 441 |  | 0 | 0 | 0 | 1
29510010 |  |  | 2 | 95 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1256.4 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1256 | 1574 | 1696 | 2082 | 108 | 135 | 146 | 179 | 0.064408 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1396 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
29510011 |  |  | 2 | 95 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1195 | 2136 | 2301 | 2825 | 103 | 184 | 198 | 243 | 0.101 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 277.45 | 298.375 | 366.575 | 0.95 | 0.95 | 0.95 | 277 | 298 | 367 | 119 | 128 | 158 | 0.13275 | 0.15241 | 0.22724 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1758 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 277 | 298 | 367 |  | 0 | 0 | 0 | 1
29510015 |  |  | 2 | 95 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1612.8 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1613 | 1799 | 1926 | 2655 | 139 | 155 | 166 | 228 | 0.10474 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 2016 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
29510016 |  |  | 2 | 95 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1822.4 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1822 | 2630 | 2817 | 3883 | 157 | 226 | 242 | 334 | 0.37912 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312.325 | 334.025 | 461.125 | 0.95 | 0.95 | 0.95 | 312 | 334 | 461 | 134 | 144 | 198 | 0.27757 | 0.3198 | 0.59878 | 2 | 7 | 7.7 | 10.7 |  | 2680 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 312 | 334 | 461 |  | 0 | 0 | 0 | 1
29510020 |  |  | 2 | 95 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2275.2 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2275 | 2519 | 2714 | 3331 | 196 | 217 | 233 | 286 | 0.16074 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2844 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
29510021 |  |  | 2 | 95 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3052.8 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3053 | 3388 | 3627 | 5000 | 263 | 291 | 312 | 430 | 0.41144 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.5476 | 364.6513 | 502.6805 | 0.85 | 0.85 | 0.85 | 341 | 365 | 503 | 147 | 157 | 216 | 0.13199 | 0.15008 | 0.27991 | 2.7 | 7 | 7.7 | 10.7 |  | 3816 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 341 | 365 | 503 |  | 0 | 0 | 0 | 1
29511010 |  |  | 2 | 95 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1382.4 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1382 | 1766 | 1903 | 2336 | 119 | 152 | 164 | 201 | 0.080603 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1536 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
29511011 |  |  | 2 | 95 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1315 | 2397 | 2582 | 3169 | 113 | 206 | 222 | 273 | 0.12603 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 311.1009 | 335.156 | 411.401 | 0.95 | 0.95 | 0.95 | 311 | 335 | 411 | 134 | 144 | 177 | 0.17385 | 0.19918 | 0.29429 | 1.5 | 8.4 | 9.3 | 14 |  | 1934 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 411 |  | 0 | 0 | 0 | 1
29511015 |  |  | 2 | 95 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1774.4 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1774 | 1908 | 2043 | 2817 | 153 | 164 | 176 | 242 | 0.12874 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2218 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
29511016 |  |  | 2 | 95 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 2004.64 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2005 | 2850 | 3051 | 4207 | 172 | 245 | 262 | 362 | 0.45958 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 316.0705 | 338.4417 | 466.55 | 0.95 | 0.95 | 0.95 | 316 | 338 | 467 | 136 | 145 | 201 | 0.28967 | 0.32853 | 0.62442 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2948 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 316 | 338 | 467 |  | 0 | 0 | 0 | 1
29511020 |  |  | 2 | 95 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2502.4 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2502 | 2693 | 2901 | 3561 | 215 | 232 | 249 | 306 | 0.19543 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 3128 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
29511021 |  |  | 2 | 95 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3356.8 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 3357 | 3556 | 3808 | 5249 | 289 | 306 | 327 | 451 | 0.50348 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 345.378 | 369.8235 | 509.8105 | 0.85 | 0.85 | 0.85 | 345 | 370 | 510 | 148 | 159 | 219 | 0.13647 | 0.15692 | 0.29292 | 2.9 | 7.9 | 8.8 | 12.5 |  | 4196 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 345 | 370 | 510 |  | 0 | 0 | 0 | 1
29512010 |  |  | 2 | 95 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1507.5 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1508 | 1925 | 2080 | 2590 | 130 | 166 | 179 | 223 | 0.098986 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1675 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
29512011 |  |  | 2 | 95 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1435 | 2612 | 2822 | 3514 | 123 | 225 | 243 | 302 | 0.15445 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 338.675 | 366.575 | 456.475 | 0.95 | 0.95 | 0.95 | 339 | 367 | 456 | 146 | 158 | 196 | 0.21327 | 0.24751 | 0.37172 | 1.6 | 8.9 | 9.9 | 14.8 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 339 | 367 | 456 |  | 0 | 0 | 0 | 1
29512015 |  |  | 2 | 95 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1935.2 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1935 | 2217 | 2374 | 3303 | 166 | 191 | 204 | 284 | 0.15369 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2419 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
29512016 |  |  | 2 | 95 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2186.88 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2187 | 3242 | 3472 | 4830 | 188 | 279 | 299 | 415 | 0.55425 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 384.4 | 412.3 | 573.5 | 0.95 | 0.95 | 0.95 | 384 | 412 | 574 | 165 | 177 | 247 | 0.42896 | 0.49236 | 0.94772 | 2.4 | 8.7 | 9.8 | 14.3 |  | 3216 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 384 | 412 | 574 |  | 0 | 0 | 0 | 1
29512020 |  |  | 2 | 95 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2730.4 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2730 | 3080 | 3327 | 4143 | 235 | 265 | 286 | 356 | 0.23578 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3413 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
29512021 |  |  | 2 | 95 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3663.2 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3663 | 4175 | 4471 | 6220 | 315 | 359 | 385 | 535 | 0.60585 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 419.7096 | 449.4497 | 625.2855 | 0.85 | 0.85 | 0.85 | 420 | 449 | 625 | 181 | 193 | 269 | 0.20585 | 0.23323 | 0.44529 | 3.2 | 8.7 | 9.8 | 14.3 |  | 4579 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 420 | 449 | 625 |  | 0 | 0 | 0 | 1
29514010 |  |  | 2 | 95 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1758.6 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1759 | 2268 | 2456 | 3098 | 151 | 195 | 211 | 266 | 0.14091 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1954 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
29514011 |  |  | 2 | 95 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1673 | 3077 | 3333 | 4203 | 144 | 265 | 287 | 361 | 0.22506 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 399.125 | 432.45 | 545.6 | 0.95 | 0.95 | 0.95 | 399 | 432 | 546 | 172 | 186 | 235 | 0.31397 | 0.36362 | 0.56421 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2461 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 399 | 432 | 546 |  | 0 | 0 | 0 | 1
29514015 |  |  | 2 | 95 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2257.6 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2258 | 2629 | 2815 | 3950 | 194 | 226 | 242 | 340 | 0.21543 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2822 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
29514016 |  |  | 2 | 95 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2551.36 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2551 | 3844 | 4117 | 5777 | 219 | 331 | 354 | 497 | 0.76578 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 456.475 | 488.25 | 685.875 | 0.95 | 0.95 | 0.95 | 456 | 488 | 686 | 196 | 210 | 295 | 0.61615 | 0.70533 | 1.3736 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3752 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 456 | 488 | 686 |  | 0 | 0 | 0 | 1
29514020 |  |  | 2 | 95 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3185.6 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3186 | 3628 | 3929 | 4956 | 274 | 312 | 338 | 426 | 0.3266 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3982 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
29514021 |  |  | 2 | 95 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4273.6 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4274 | 4951 | 5302 | 7440 | 368 | 426 | 456 | 640 | 0.84696 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 497.7249 | 533.0285 | 747.8905 | 0.85 | 0.85 | 0.85 | 498 | 533 | 748 | 214 | 229 | 322 | 0.29547 | 0.33696 | 0.65322 | 3.7 | 9.6 | 10.5 | 16.1 |  | 5342 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 498 | 533 | 748 |  | 0 | 0 | 0 | 1
3205010 |  |  | 3 | 20 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 295.2 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 295 | 649 | 695 | 812 | 25 | 56 | 60 | 70 | 0.0029866 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 328 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3206010 |  |  | 3 | 20 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 353.7 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 354 | 842 | 901 | 1066 | 30 | 72 | 77 | 92 | 0.0045345 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 393 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3206015 |  |  | 3 | 20 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 523.2 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 523 | 957 | 1028 | 1360 | 45 | 82 | 88 | 117 | 0.010483 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 654 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3206020 |  |  | 3 | 20 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 735.2 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 735 | 1347 | 1442 | 1706 | 63 | 116 | 124 | 147 | 0.016079 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 919 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3207010 |  |  | 3 | 20 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 413.1 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 413 | 1030 | 1104 | 1320 | 36 | 89 | 95 | 114 | 0.0068312 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 459 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3207015 |  |  | 3 | 20 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 610.4 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 610 | 1071 | 1150 | 1521 | 52 | 92 | 99 | 131 | 0.014301 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 763 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3207020 |  |  | 3 | 20 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 857.6 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 858 | 1510 | 1619 | 1936 | 74 | 130 | 139 | 166 | 0.022511 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1072 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3208010 |  |  | 3 | 20 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 471.6 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 472 | 1214 | 1304 | 1574 | 41 | 104 | 112 | 135 | 0.0092533 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 524 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3208015 |  |  | 3 | 20 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 697.6 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 698 | 1395 | 1496 | 2008 | 60 | 120 | 129 | 173 | 0.019408 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 872 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3208020 |  |  | 3 | 20 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 980.8 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 981 | 1943 | 2086 | 2518 | 84 | 167 | 179 | 217 | 0.029418 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1226 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3209010 |  |  | 3 | 20 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 531 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 531 | 1396 | 1501 | 1828 | 46 | 120 | 129 | 157 | 0.012122 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 590 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3209015 |  |  | 3 | 20 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 784.8 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 785 | 1598 | 1712 | 2331 | 68 | 137 | 147 | 200 | 0.025381 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 981 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3209020 |  |  | 3 | 20 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1103.2 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1103 | 2233 | 2402 | 2925 | 95 | 192 | 207 | 252 | 0.038119 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1379 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
32010010 |  |  | 3 | 20 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 589.5 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 590 | 1574 | 1696 | 2082 | 51 | 135 | 146 | 179 | 0.015464 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 655 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
32010015 |  |  | 3 | 20 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 872 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 872 | 1799 | 1926 | 2655 | 75 | 155 | 166 | 228 | 0.031429 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1090 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
32010020 |  |  | 3 | 20 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1225.6 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1226 | 2519 | 2714 | 3331 | 105 | 217 | 233 | 286 | 0.04716 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 1532 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
32011010 |  |  | 3 | 20 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 648.9 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 649 | 1766 | 1903 | 2336 | 56 | 152 | 164 | 201 | 0.019303 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 721 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
32011015 |  |  | 3 | 20 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 959.2 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 959 | 1908 | 2043 | 2817 | 82 | 164 | 176 | 242 | 0.038209 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1199 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
32011020 |  |  | 3 | 20 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1348 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1348 | 2693 | 2901 | 3561 | 116 | 232 | 249 | 306 | 0.058241 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 1685 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
32012010 |  |  | 3 | 20 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 707.4 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 707 | 1925 | 2080 | 2590 | 61 | 166 | 179 | 223 | 0.023662 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 786 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
32012015 |  |  | 3 | 20 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1046.4 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1046 | 2217 | 2374 | 3303 | 90 | 191 | 204 | 284 | 0.046746 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1308 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
32012020 |  |  | 3 | 20 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1470.4 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 1470 | 3080 | 3327 | 4143 | 126 | 265 | 286 | 356 | 0.069519 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 1838 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
32014010 |  |  | 3 | 20 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 825.3 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 825 | 2268 | 2456 | 3098 | 71 | 195 | 211 | 266 | 0.034037 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 917 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
32014015 |  |  | 3 | 20 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1220.8 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1221 | 2629 | 2815 | 3950 | 105 | 226 | 242 | 340 | 0.065547 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 1526 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
32014020 |  |  | 3 | 20 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 1716 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1716 | 3628 | 3929 | 4956 | 148 | 312 | 338 | 426 | 0.097985 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 2145 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
32016010 |  |  | 3 | 20 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 943.2 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 943 | 2604 | 2827 | 3605 | 81 | 224 | 243 | 310 | 0.04677 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1048 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
32016015 |  |  | 3 | 20 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1395.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1395 | 3021 | 3226 | 4598 | 120 | 260 | 277 | 395 | 0.088009 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 1744 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
32016020 |  |  | 3 | 20 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 1960.8 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1961 | 4166 | 4522 | 5768 | 169 | 358 | 389 | 496 | 0.13039 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 2451 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
32018010 |  |  | 3 | 20 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1061.1 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1061 | 2971 | 3225 | 4113 | 91 | 256 | 277 | 354 | 0.062033 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1179 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
32018015 |  |  | 3 | 20 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1569.6 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 1570 | 3233 | 3452 | 4921 | 135 | 278 | 297 | 423 | 0.11431 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 1962 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
32018020 |  |  | 3 | 20 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2206.4 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2206 | 4498 | 4883 | 6228 | 190 | 387 | 420 | 536 | 0.16799 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 2758 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
32020010 |  |  | 3 | 20 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1179 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1179 | 3260 | 3553 | 4621 | 101 | 280 | 306 | 397 | 0.079996 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1310 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
32020015 |  |  | 3 | 20 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 1744 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1744 | 3875 | 4083 | 5893 | 150 | 333 | 351 | 507 | 0.1446 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 2180 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
32020020 |  |  | 3 | 20 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 2451.2 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2451 | 5215 | 5684 | 7393 | 211 | 448 | 489 | 636 | 0.21097 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 3064 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
32022010 |  |  | 3 | 20 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1296.9 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1297 | 3561 | 3891 | 5129 | 112 | 306 | 335 | 441 | 0.10251 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 1441 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
32022015 |  |  | 3 | 20 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 1918.4 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1918 | 4303 | 4482 | 6541 | 165 | 370 | 385 | 563 | 0.17905 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 2398 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
32022020 |  |  | 3 | 20 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 2696 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2696 | 5697 | 6224 | 8205 | 232 | 490 | 535 | 706 | 0.2595 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 3370 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
32024010 |  |  | 3 | 20 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1414.8 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 3860 | 4229 | 5637 | 122 | 332 | 364 | 485 | 0.12657 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 1572 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
32024015 |  |  | 3 | 20 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2092.8 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2093 | 4730 | 4902 | 7188 | 180 | 407 | 422 | 618 | 0.21782 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 2616 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
32024020 |  |  | 3 | 20 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 2941.6 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2942 | 6176 | 6766 | 9018 | 253 | 531 | 582 | 776 | 0.31376 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 3677 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
32026010 |  |  | 3 | 20 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1532.7 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1533 | 4178 | 4608 | 6144 | 132 | 359 | 396 | 528 | 0.15383 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 1703 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
32026015 |  |  | 3 | 20 | 260 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2267.2 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.08 | 1.08 | 1.08 | 2267 | 5669 | 6253 | 8337 | 195 | 488 | 538 | 717 | 0.26106 | 1.5103 | 1.8217 | 3.1664 | 0.0002083 | 1.724 | 2 | 0.00046183 | 949.5112 | 1047.255 | 1396.34 | 1.01 | 1.01 | 1.01 | 950 | 1047 | 1396 | 409 | 450 | 600 | 1.0761 | 1.2926 | 2.2469 | 2.6 | 16.2 | 18.6 | 31.4 |  | 2834 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
32026020 |  |  | 3 | 20 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3186.4 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3186 | 6445 | 7108 | 9477 | 274 | 554 | 611 | 815 | 0.37389 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 3983 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
32028010 |  |  | 3 | 20 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1650.6 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 1651 | 4331 | 4782 | 6370 | 142 | 372 | 411 | 548 | 0.18441 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 1834 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
32028015 |  |  | 3 | 20 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 2441.6 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 2442 | 5584 | 5709 | 8484 | 210 | 480 | 491 | 730 | 0.30891 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 3052 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
32028020 |  |  | 3 | 20 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 3432 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 3432 | 7237 | 7990 | 10642 | 295 | 622 | 687 | 915 | 0.44007 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 4290 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
3305010 |  |  | 3 | 30 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 371.7 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 372 | 649 | 695 | 812 | 32 | 56 | 60 | 70 | 0.0048168 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 413 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3305011 |  |  | 3 | 30 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 381.48 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 381 | 881 | 943 | 1102 | 33 | 76 | 81 | 95 | 0.0085136 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 561 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1
3306010 |  |  | 3 | 30 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 446.4 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 446 | 842 | 901 | 1066 | 38 | 72 | 77 | 92 | 0.0071491 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 496 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3306011 |  |  | 3 | 30 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 457.64 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 458 | 1142 | 1223 | 1447 | 39 | 98 | 105 | 124 | 0.012641 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 673 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1
3306015 |  |  | 3 | 30 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 652 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 652 | 957 | 1028 | 1360 | 56 | 82 | 88 | 117 | 0.016115 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 815 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3306016 |  |  | 3 | 30 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 603.84 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 604 | 1400 | 1503 | 1989 | 52 | 120 | 129 | 171 | 0.040291 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 888 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1
3306020 |  |  | 3 | 30 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 915.2 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 915 | 1347 | 1442 | 1706 | 79 | 116 | 124 | 147 | 0.025146 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1144 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3306021 |  |  | 3 | 30 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 935.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 935 | 1803 | 1935 | 2561 | 80 | 155 | 166 | 220 | 0.036566 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1169 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1
3307010 |  |  | 3 | 30 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 520.2 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 520 | 1030 | 1104 | 1320 | 45 | 89 | 95 | 114 | 0.010479 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 578 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3307011 |  |  | 3 | 30 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 533.8 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 534 | 1397 | 1498 | 1791 | 46 | 120 | 129 | 154 | 0.018535 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 785 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1
3307015 |  |  | 3 | 30 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 760.8 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 761 | 1071 | 1150 | 1521 | 65 | 92 | 99 | 131 | 0.022152 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 951 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3307016 |  |  | 3 | 30 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 704.48 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 704 | 1628 | 1747 | 2313 | 61 | 140 | 150 | 199 | 0.056221 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1036 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1
3307020 |  |  | 3 | 30 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1067.2 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1067 | 1510 | 1619 | 1936 | 92 | 130 | 139 | 166 | 0.034586 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1334 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3307021 |  |  | 3 | 30 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1091 | 1978 | 2123 | 2810 | 94 | 170 | 183 | 242 | 0.051472 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1364 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1
3308010 |  |  | 3 | 30 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 594.9 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 595 | 1214 | 1304 | 1574 | 51 | 104 | 112 | 135 | 0.014039 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 661 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3308011 |  |  | 3 | 30 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 609.96 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 610 | 1648 | 1770 | 2136 | 52 | 142 | 152 | 184 | 0.024889 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 897 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
3308015 |  |  | 3 | 30 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 869.6 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 870 | 1395 | 1496 | 2008 | 75 | 120 | 129 | 173 | 0.030034 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1087 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3308016 |  |  | 3 | 30 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 805.12 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 805 | 2040 | 2188 | 2936 | 69 | 175 | 188 | 252 | 0.072911 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1184 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
3308020 |  |  | 3 | 30 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1220 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1220 | 1943 | 2086 | 2518 | 105 | 167 | 179 | 217 | 0.045649 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1525 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3308021 |  |  | 3 | 30 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1246.4 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1246 | 2628 | 2818 | 3781 | 107 | 226 | 242 | 325 | 0.067937 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 1558 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1
3309010 |  |  | 3 | 30 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 668.7 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 669 | 1396 | 1501 | 1828 | 58 | 120 | 129 | 157 | 0.018845 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 743 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3309011 |  |  | 3 | 30 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 686.12 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 686 | 1894 | 2037 | 2480 | 59 | 163 | 175 | 213 | 0.033465 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1009 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1
3309015 |  |  | 3 | 30 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 978.4 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 978 | 1598 | 1712 | 2331 | 84 | 137 | 147 | 200 | 0.038346 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1223 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3309016 |  |  | 3 | 30 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 905.76 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 906 | 2337 | 2503 | 3409 | 78 | 201 | 215 | 293 | 0.094327 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1332 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
3309020 |  |  | 3 | 30 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1372 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1372 | 2233 | 2402 | 2925 | 118 | 192 | 207 | 252 | 0.058376 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1715 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3309021 |  |  | 3 | 30 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1402.4 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1402 | 3009 | 3224 | 4391 | 121 | 259 | 277 | 378 | 0.088367 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 1753 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
33010010 |  |  | 3 | 30 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 743.4 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 743 | 1574 | 1696 | 2082 | 64 | 135 | 146 | 179 | 0.023791 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 826 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
33010011 |  |  | 3 | 30 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 762.28 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 762 | 2136 | 2301 | 2825 | 66 | 184 | 198 | 243 | 0.043598 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1121 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
33010015 |  |  | 3 | 30 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1087.2 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1087 | 1799 | 1926 | 2655 | 93 | 155 | 166 | 228 | 0.047796 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1359 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
33010016 |  |  | 3 | 30 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1006.4 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1006 | 2630 | 2817 | 3883 | 87 | 226 | 242 | 334 | 0.11874 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1480 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
33010020 |  |  | 3 | 30 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1524.8 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1525 | 2519 | 2714 | 3331 | 131 | 217 | 233 | 286 | 0.072807 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 1906 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
33010021 |  |  | 3 | 30 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1558.4 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 1558 | 3388 | 3627 | 5000 | 134 | 291 | 312 | 430 | 0.11017 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 1948 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
33011010 |  |  | 3 | 30 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 818.1 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 818 | 1766 | 1903 | 2336 | 70 | 152 | 164 | 201 | 0.029441 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 909 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
33011011 |  |  | 3 | 30 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 838.44 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 838 | 2397 | 2582 | 3169 | 72 | 206 | 222 | 273 | 0.053959 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1233 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
33011015 |  |  | 3 | 30 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1196 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1196 | 1908 | 2043 | 2817 | 103 | 164 | 176 | 242 | 0.059538 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1495 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
33011016 |  |  | 3 | 30 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1107.04 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1107 | 2850 | 3051 | 4207 | 95 | 245 | 262 | 362 | 0.14323 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 1628 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
33011020 |  |  | 3 | 30 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1677.6 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1678 | 2693 | 2901 | 3561 | 144 | 232 | 249 | 306 | 0.088979 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2097 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
33011021 |  |  | 3 | 30 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1714.4 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 1714 | 3556 | 3808 | 5249 | 147 | 306 | 327 | 451 | 0.13468 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2143 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
33012010 |  |  | 3 | 30 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 891.9 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 892 | 1925 | 2080 | 2590 | 77 | 166 | 179 | 223 | 0.036723 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 991 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
33012011 |  |  | 3 | 30 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 914.6 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 915 | 2612 | 2822 | 3514 | 79 | 225 | 243 | 302 | 0.06728 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1345 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
33012015 |  |  | 3 | 30 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1304.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1305 | 2217 | 2374 | 3303 | 112 | 191 | 204 | 284 | 0.071478 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1631 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
33012016 |  |  | 3 | 30 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1207.68 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1208 | 3242 | 3472 | 4830 | 104 | 279 | 299 | 415 | 0.17351 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 1776 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
33012020 |  |  | 3 | 30 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 1829.6 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 1830 | 3080 | 3327 | 4143 | 157 | 265 | 286 | 356 | 0.10693 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2287 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
33012021 |  |  | 3 | 30 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 1870.4 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 1870 | 4175 | 4471 | 6220 | 161 | 359 | 385 | 535 | 0.16394 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 2338 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
33014010 |  |  | 3 | 30 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1040.4 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1040 | 2268 | 2456 | 3098 | 89 | 195 | 211 | 266 | 0.05203 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1156 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
33014011 |  |  | 3 | 30 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1066.92 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1067 | 3077 | 3333 | 4203 | 92 | 265 | 287 | 361 | 0.097449 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1569 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
33014015 |  |  | 3 | 30 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1522.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1522 | 2629 | 2815 | 3950 | 131 | 226 | 242 | 340 | 0.10058 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 1903 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
33014016 |  |  | 3 | 30 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1408.96 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1409 | 3844 | 4117 | 5777 | 121 | 331 | 354 | 497 | 0.23981 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2072 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
33014020 |  |  | 3 | 30 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2134.4 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2134 | 3628 | 3929 | 4956 | 184 | 312 | 338 | 426 | 0.14989 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 2668 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
33014021 |  |  | 3 | 30 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2181.6 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2182 | 4951 | 5302 | 7440 | 188 | 426 | 456 | 640 | 0.22986 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 2727 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
33016010 |  |  | 3 | 30 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1189.8 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1190 | 2604 | 2827 | 3605 | 102 | 224 | 243 | 310 | 0.071986 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1322 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
33016011 |  |  | 3 | 30 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1219.92 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1220 | 3533 | 3835 | 4892 | 105 | 304 | 330 | 421 | 0.13467 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 1794 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
33016015 |  |  | 3 | 30 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1739.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 1739 | 3021 | 3226 | 4598 | 150 | 260 | 277 | 395 | 0.13538 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2174 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
33016016 |  |  | 3 | 30 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1610.24 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1610 | 4418 | 4717 | 6724 | 138 | 380 | 406 | 578 | 0.31805 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 2368 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
33016020 |  |  | 3 | 30 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2440 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 2440 | 4166 | 4522 | 5768 | 210 | 358 | 389 | 496 | 0.19906 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3050 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
33016021 |  |  | 3 | 30 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2493.6 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 2494 | 5690 | 6075 | 8659 | 214 | 489 | 522 | 745 | 0.30577 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 3117 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
33018010 |  |  | 3 | 30 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1338.3 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1338 | 2971 | 3225 | 4113 | 115 | 256 | 277 | 354 | 0.09597 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1487 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
33018011 |  |  | 3 | 30 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1372.24 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1372 | 4031 | 4376 | 5581 | 118 | 347 | 376 | 480 | 0.1795 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2018 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
33018015 |  |  | 3 | 30 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 1956.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 1957 | 3233 | 3452 | 4921 | 168 | 278 | 297 | 423 | 0.17413 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 2446 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
33018016 |  |  | 3 | 30 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1811.52 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 1812 | 4843 | 5171 | 7371 | 156 | 417 | 445 | 634 | 0.41383 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 2664 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
33018020 |  |  | 3 | 30 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2744.8 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2745 | 4498 | 4883 | 6228 | 236 | 387 | 420 | 536 | 0.25604 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 3431 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
33018021 |  |  | 3 | 30 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2804.8 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2805 | 6017 | 6424 | 9157 | 241 | 517 | 552 | 788 | 0.39734 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 3506 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
33020010 |  |  | 3 | 30 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1486.8 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1487 | 3260 | 3553 | 4621 | 128 | 280 | 306 | 397 | 0.12425 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1652 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
33020011 |  |  | 3 | 30 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1524.56 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1525 | 4423 | 4821 | 6270 | 131 | 380 | 415 | 539 | 0.23247 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2242 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
33020015 |  |  | 3 | 30 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2174.4 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2174 | 3875 | 4083 | 5893 | 187 | 333 | 351 | 507 | 0.22081 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 2718 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
33020016 |  |  | 3 | 30 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2012.8 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2013 | 5667 | 5971 | 8618 | 173 | 487 | 514 | 741 | 0.51789 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 2960 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
33020020 |  |  | 3 | 30 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3049.6 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3050 | 5215 | 5684 | 7393 | 262 | 448 | 489 | 636 | 0.32108 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 3812 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
33020021 |  |  | 3 | 30 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3116.8 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3117 | 7299 | 7690 | 11098 | 268 | 628 | 661 | 954 | 0.50277 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 3896 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
33022010 |  |  | 3 | 30 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1635.3 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1635 | 3561 | 3891 | 5129 | 141 | 306 | 335 | 441 | 0.15708 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 1817 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
33022011 |  |  | 3 | 30 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1676.88 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1677 | 4831 | 5279 | 6959 | 144 | 415 | 454 | 598 | 0.29407 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2466 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
33022015 |  |  | 3 | 30 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2392 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2392 | 4303 | 4482 | 6541 | 206 | 370 | 385 | 563 | 0.27392 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 2990 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
33022016 |  |  | 3 | 30 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2214.08 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2214 | 6292 | 6554 | 9565 | 190 | 541 | 564 | 823 | 0.63516 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 3256 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
33022020 |  |  | 3 | 30 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3354.4 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3354 | 5697 | 6224 | 8205 | 288 | 490 | 535 | 706 | 0.39443 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 4193 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
33022021 |  |  | 3 | 30 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 3428.8 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3429 | 8103 | 8440 | 12318 | 295 | 697 | 726 | 1059 | 0.62259 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 4286 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
33024010 |  |  | 3 | 30 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 1783.8 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1784 | 3860 | 4229 | 5637 | 153 | 332 | 364 | 485 | 0.19238 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 1982 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
33024011 |  |  | 3 | 30 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 1829.2 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1829 | 5238 | 5738 | 7648 | 157 | 450 | 493 | 658 | 0.36483 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 2690 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
33024015 |  |  | 3 | 30 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2609.6 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2610 | 4730 | 4902 | 7188 | 224 | 407 | 422 | 618 | 0.33087 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 3262 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
33024016 |  |  | 3 | 30 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2415.36 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2415 | 6916 | 7168 | 10512 | 208 | 595 | 616 | 904 | 0.77319 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 3552 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
33024020 |  |  | 3 | 30 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3659.2 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3659 | 6176 | 6766 | 9018 | 315 | 531 | 582 | 776 | 0.47927 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 4574 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
33024021 |  |  | 3 | 30 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 3740 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3740 | 8907 | 9231 | 13538 | 322 | 766 | 794 | 1164 | 0.75731 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 4675 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
33026010 |  |  | 3 | 30 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 1933.2 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1933 | 4178 | 4608 | 6144 | 166 | 359 | 396 | 528 | 0.23477 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2148 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
33026011 |  |  | 3 | 30 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 1982.2 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1982 | 5669 | 6253 | 8337 | 170 | 488 | 538 | 717 | 0.44522 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 2915 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
33026015 |  |  | 3 | 30 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 2826.4 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 2826 | 4942 | 5122 | 7511 | 243 | 425 | 440 | 646 | 0.39726 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 3533 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
33026016 |  |  | 3 | 30 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2616.64 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2617 | 7342 | 7610 | 11159 | 225 | 631 | 654 | 960 | 0.9187 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 3848 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
33026020 |  |  | 3 | 30 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 3964.8 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3965 | 6445 | 7108 | 9477 | 341 | 554 | 611 | 815 | 0.57025 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 4956 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
33026021 |  |  | 3 | 30 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4052 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4052 | 9235 | 9571 | 14035 | 348 | 794 | 823 | 1207 | 0.90248 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 5065 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
33028010 |  |  | 3 | 30 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2081.7 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2082 | 4331 | 4782 | 6370 | 179 | 372 | 411 | 548 | 0.28244 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 2313 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
33028011 |  |  | 3 | 30 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2134.52 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2135 | 5977 | 6599 | 8790 | 184 | 514 | 568 | 756 | 0.54109 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3139 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
33028015 |  |  | 3 | 30 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3044 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3044 | 5584 | 5709 | 8484 | 262 | 480 | 491 | 730 | 0.47075 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 3805 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
33028016 |  |  | 3 | 30 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 2817.92 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2818 | 8166 | 8348 | 12406 | 242 | 702 | 718 | 1067 | 1.0786 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 4144 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
33028020 |  |  | 3 | 30 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4269.6 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 4270 | 7237 | 7990 | 10642 | 367 | 622 | 687 | 915 | 0.67026 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 5337 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
33028021 |  |  | 3 | 30 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4363.2 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 4363 | 10516 | 10751 | 15977 | 375 | 904 | 925 | 1374 | 1.068 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 5454 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
33030010 |  |  | 3 | 30 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2230.2 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 2230 | 4485 | 4951 | 6595 | 192 | 386 | 426 | 567 | 0.33562 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 2478 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
33030011 |  |  | 3 | 30 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2286.84 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 2287 | 6285 | 6939 | 9242 | 197 | 541 | 597 | 795 | 0.64275 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 0.95 | 0.95 | 0.95 | 963 | 1063 | 1416 | 414 | 457 | 609 | 2.5034 | 3.0019 | 5.0929 | 4 | 16.2 | 18.6 | 31.4 |  | 3363 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 963 | 1063 | 1416 |  | 0 | 0 | 0 | 1
33030015 |  |  | 3 | 30 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3261.6 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 3262 | 5796 | 5926 | 8806 | 281 | 498 | 510 | 757 | 0.55158 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 4077 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
33030016 |  |  | 3 | 30 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3019.2 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 3019 | 8592 | 8784 | 13053 | 260 | 739 | 755 | 1123 | 1.2624 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 0.95 | 0.95 | 0.95 | 1260 | 1288 | 1915 | 542 | 554 | 823 | 5.2152 | 5.441 | 11.7219 | 6 | 19.3 | 20.4 | 34.5 |  | 4440 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1260 | 1288 | 1915 |  | 0 | 0 | 0 | 1
33030020 |  |  | 3 | 30 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4574.4 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 4574 | 7549 | 8335 | 11102 | 393 | 649 | 717 | 955 | 0.77952 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 5718 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
33030021 |  |  | 3 | 30 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4675.2 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 4675 | 10844 | 11086 | 16475 | 402 | 933 | 953 | 1417 | 1.25 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 0.85 | 0.85 | 0.85 | 1468 | 1501 | 2231 | 631 | 645 | 959 | 2.9532 | 3.0797 | 6.5811 | 8 | 19.3 | 20.4 | 34.5 |  | 5844 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1468 | 1501 | 2231 |  | 0 | 0 | 0 | 1
3405010 |  |  | 3 | 40 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 433.8 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 434 | 649 | 695 | 812 | 37 | 56 | 60 | 70 | 0.0063825 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 482 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3405011 |  |  | 3 | 40 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 429.76 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 430 | 881 | 943 | 1102 | 37 | 76 | 81 | 95 | 0.010613 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 632 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1
3406010 |  |  | 3 | 40 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 520.2 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 520 | 842 | 901 | 1066 | 45 | 72 | 77 | 92 | 0.0099056 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 578 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3406011 |  |  | 3 | 40 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 515.44 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 515 | 1142 | 1223 | 1447 | 44 | 98 | 105 | 124 | 0.015927 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 758 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1
3406015 |  |  | 3 | 40 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 752.8 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 753 | 957 | 1028 | 1360 | 65 | 82 | 88 | 117 | 0.021607 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 941 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3406016 |  |  | 3 | 40 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 693.6 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 694 | 1400 | 1503 | 1989 | 60 | 120 | 129 | 171 | 0.053468 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1020 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1
3406020 |  |  | 3 | 40 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1054.4 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1054 | 1347 | 1442 | 1706 | 91 | 116 | 124 | 147 | 0.033257 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1318 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3406021 |  |  | 3 | 40 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1091.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1091 | 1803 | 1935 | 2561 | 94 | 155 | 166 | 220 | 0.050223 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1364 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1
3407010 |  |  | 3 | 40 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 606.6 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 607 | 1030 | 1104 | 1320 | 52 | 89 | 95 | 114 | 0.013833 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 674 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3407011 |  |  | 3 | 40 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 601.8 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 602 | 1397 | 1498 | 1791 | 52 | 120 | 129 | 154 | 0.023415 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 885 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1
3407015 |  |  | 3 | 40 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 878.4 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 878 | 1071 | 1150 | 1521 | 76 | 92 | 99 | 131 | 0.030109 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1098 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3407016 |  |  | 3 | 40 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 809.2 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 809 | 1628 | 1747 | 2313 | 70 | 140 | 150 | 199 | 0.073769 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1190 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1
3407020 |  |  | 3 | 40 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1229.6 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1230 | 1510 | 1619 | 1936 | 106 | 130 | 139 | 166 | 0.045741 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1537 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3407021 |  |  | 3 | 40 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1273.6 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1274 | 1978 | 2123 | 2810 | 110 | 170 | 183 | 242 | 0.070079 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1592 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1
3408010 |  |  | 3 | 40 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 693 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 693 | 1214 | 1304 | 1574 | 60 | 104 | 112 | 135 | 0.019158 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 770 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3408011 |  |  | 3 | 40 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 687.48 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 687 | 1648 | 1770 | 2136 | 59 | 142 | 152 | 184 | 0.03163 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1011 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
3408015 |  |  | 3 | 40 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1003.2 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1003 | 1395 | 1496 | 2008 | 86 | 120 | 129 | 173 | 0.039267 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1254 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3408016 |  |  | 3 | 40 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 924.8 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 925 | 2040 | 2188 | 2936 | 80 | 175 | 188 | 252 | 0.097585 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1360 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
3408020 |  |  | 3 | 40 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1405.6 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1406 | 1943 | 2086 | 2518 | 121 | 167 | 179 | 217 | 0.060366 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1757 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3408021 |  |  | 3 | 40 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1455.2 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1455 | 2628 | 2818 | 3781 | 125 | 226 | 242 | 325 | 0.092125 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 1819 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1
3409010 |  |  | 3 | 40 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 780.3 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 780 | 1396 | 1501 | 1828 | 67 | 120 | 129 | 157 | 0.024809 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 867 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3409011 |  |  | 3 | 40 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 773.84 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 774 | 1894 | 2037 | 2480 | 67 | 163 | 175 | 213 | 0.042562 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1138 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1
3409015 |  |  | 3 | 40 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1128.8 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1129 | 1598 | 1712 | 2331 | 97 | 137 | 147 | 200 | 0.0508 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1411 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3409016 |  |  | 3 | 40 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1040.4 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1040 | 2337 | 2503 | 3409 | 89 | 201 | 215 | 293 | 0.12228 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1530 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
3409020 |  |  | 3 | 40 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1580.8 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1581 | 2233 | 2402 | 2925 | 136 | 192 | 207 | 252 | 0.077185 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 1976 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3409021 |  |  | 3 | 40 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1637.6 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1638 | 3009 | 3224 | 4391 | 141 | 259 | 277 | 378 | 0.11917 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 2047 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
34010010 |  |  | 3 | 40 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 866.7 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 867 | 1574 | 1696 | 2082 | 75 | 135 | 146 | 179 | 0.032159 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 963 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
34010011 |  |  | 3 | 40 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 859.52 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 860 | 2136 | 2301 | 2825 | 74 | 184 | 198 | 243 | 0.05409 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1264 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
34010015 |  |  | 3 | 40 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1254.4 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1254 | 1799 | 1926 | 2655 | 108 | 155 | 166 | 228 | 0.063986 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1568 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
34010016 |  |  | 3 | 40 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1156 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1156 | 2630 | 2817 | 3883 | 99 | 226 | 242 | 334 | 0.15305 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1700 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
34010020 |  |  | 3 | 40 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1756.8 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1757 | 2519 | 2714 | 3331 | 151 | 217 | 233 | 286 | 0.096247 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2196 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
34010021 |  |  | 3 | 40 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 1819.2 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 1819 | 3388 | 3627 | 5000 | 156 | 291 | 312 | 430 | 0.14822 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2274 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
34011010 |  |  | 3 | 40 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 953.1 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 953 | 1766 | 1903 | 2336 | 82 | 152 | 164 | 201 | 0.039734 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1059 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
34011011 |  |  | 3 | 40 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 945.2 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 945 | 2397 | 2582 | 3169 | 81 | 206 | 222 | 273 | 0.067326 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1390 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
34011015 |  |  | 3 | 40 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1380 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1380 | 1908 | 2043 | 2817 | 119 | 164 | 176 | 242 | 0.078871 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1725 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
34011016 |  |  | 3 | 40 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1271.6 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1272 | 2850 | 3051 | 4207 | 109 | 245 | 262 | 362 | 0.18758 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 1870 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
34011020 |  |  | 3 | 40 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1932.8 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1933 | 2693 | 2901 | 3561 | 166 | 232 | 249 | 306 | 0.1176 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2416 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
34011021 |  |  | 3 | 40 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2000.8 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2001 | 3556 | 3808 | 5249 | 172 | 306 | 327 | 451 | 0.18288 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2501 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
34012010 |  |  | 3 | 40 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1040.4 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1040 | 1925 | 2080 | 2590 | 89 | 166 | 179 | 223 | 0.048286 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1156 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
34012011 |  |  | 3 | 40 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1031.56 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1032 | 2612 | 2822 | 3514 | 89 | 225 | 243 | 302 | 0.08412 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1517 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
34012015 |  |  | 3 | 40 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1505.6 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1506 | 2217 | 2374 | 3303 | 130 | 191 | 204 | 284 | 0.095501 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 1882 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
34012016 |  |  | 3 | 40 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1387.2 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1387 | 3242 | 3472 | 4830 | 119 | 279 | 299 | 415 | 0.22594 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2040 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
34012020 |  |  | 3 | 40 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2108 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2108 | 3080 | 3327 | 4143 | 181 | 265 | 286 | 356 | 0.1413 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2635 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
34012021 |  |  | 3 | 40 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2183.2 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2183 | 4175 | 4471 | 6220 | 188 | 359 | 385 | 535 | 0.22162 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 2729 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
34014010 |  |  | 3 | 40 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1213.2 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1213 | 2268 | 2456 | 3098 | 104 | 195 | 211 | 266 | 0.069746 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1348 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
34014011 |  |  | 3 | 40 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1203.6 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1204 | 3077 | 3333 | 4203 | 104 | 265 | 287 | 361 | 0.12249 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1770 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
34014015 |  |  | 3 | 40 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1756 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1756 | 2629 | 2815 | 3950 | 151 | 226 | 242 | 340 | 0.13247 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2195 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
34014016 |  |  | 3 | 40 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1618.4 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1618 | 3844 | 4117 | 5777 | 139 | 331 | 354 | 497 | 0.31448 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2380 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
34014020 |  |  | 3 | 40 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2459.2 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2459 | 3628 | 3929 | 4956 | 211 | 312 | 338 | 426 | 0.19589 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3074 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
34014021 |  |  | 3 | 40 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2547.2 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2547 | 4951 | 5302 | 7440 | 219 | 426 | 456 | 640 | 0.309 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 3184 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
34016010 |  |  | 3 | 40 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1386.9 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1387 | 2604 | 2827 | 3605 | 119 | 224 | 243 | 310 | 0.096097 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1541 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
34016011 |  |  | 3 | 40 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1374.96 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1375 | 3533 | 3835 | 4892 | 118 | 304 | 330 | 421 | 0.16729 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 2022 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
34016015 |  |  | 3 | 40 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2007.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2007 | 3021 | 3226 | 4598 | 173 | 260 | 277 | 395 | 0.17836 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2509 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
34016016 |  |  | 3 | 40 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 1849.6 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1850 | 4418 | 4717 | 6724 | 159 | 380 | 406 | 578 | 0.41926 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 2720 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
34016020 |  |  | 3 | 40 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 2811.2 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 2811 | 4166 | 4522 | 5768 | 242 | 358 | 389 | 496 | 0.26249 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3514 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
34016021 |  |  | 3 | 40 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 2910.4 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 2910 | 5690 | 6075 | 8659 | 250 | 489 | 522 | 745 | 0.41297 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 3638 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
34018010 |  |  | 3 | 40 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1559.7 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1560 | 2971 | 3225 | 4113 | 134 | 256 | 277 | 354 | 0.12769 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1733 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
34018011 |  |  | 3 | 40 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1547 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1547 | 4031 | 4376 | 5581 | 133 | 347 | 376 | 480 | 0.22402 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2275 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
34018015 |  |  | 3 | 40 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2257.6 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2258 | 3233 | 3452 | 4921 | 194 | 278 | 297 | 423 | 0.22979 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 2822 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
34018016 |  |  | 3 | 40 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2080.8 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2081 | 4843 | 5171 | 7371 | 179 | 417 | 445 | 634 | 0.54084 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3060 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
34018020 |  |  | 3 | 40 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3162.4 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3162 | 4498 | 4883 | 6228 | 272 | 387 | 420 | 536 | 0.33751 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 3953 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
34018021 |  |  | 3 | 40 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3274.4 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3274 | 6017 | 6424 | 9157 | 282 | 517 | 552 | 788 | 0.53791 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 4093 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
34020010 |  |  | 3 | 40 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1733.4 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1733 | 3260 | 3553 | 4621 | 149 | 280 | 306 | 397 | 0.16487 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 1926 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
34020011 |  |  | 3 | 40 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1719.04 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1719 | 4423 | 4821 | 6270 | 148 | 380 | 415 | 539 | 0.29119 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2528 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
34020015 |  |  | 3 | 40 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2508.8 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2509 | 3875 | 4083 | 5893 | 216 | 333 | 351 | 507 | 0.29135 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3136 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
34020016 |  |  | 3 | 40 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2312 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2312 | 5667 | 5971 | 8618 | 199 | 487 | 514 | 741 | 0.67977 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3400 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
34020020 |  |  | 3 | 40 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3513.6 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3514 | 5215 | 5684 | 7393 | 302 | 448 | 489 | 636 | 0.42311 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4392 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
34020021 |  |  | 3 | 40 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 3638.4 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3638 | 7299 | 7690 | 11098 | 313 | 628 | 661 | 954 | 0.67767 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 4548 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
34022010 |  |  | 3 | 40 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 1907.1 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1907 | 3561 | 3891 | 5129 | 164 | 306 | 335 | 441 | 0.20795 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2119 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
34022011 |  |  | 3 | 40 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 1891.08 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1891 | 4831 | 5279 | 6959 | 163 | 415 | 454 | 598 | 0.36944 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 2781 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
34022015 |  |  | 3 | 40 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 2760 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2760 | 4303 | 4482 | 6541 | 237 | 370 | 385 | 563 | 0.35846 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3450 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
34022016 |  |  | 3 | 40 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2543.2 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2543 | 6292 | 6554 | 9565 | 219 | 541 | 564 | 823 | 0.83658 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 3740 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
34022020 |  |  | 3 | 40 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 3864.8 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 3865 | 5697 | 6224 | 8205 | 332 | 490 | 535 | 706 | 0.51961 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 4831 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
34022021 |  |  | 3 | 40 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4002.4 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4002 | 8103 | 8440 | 12318 | 344 | 697 | 726 | 1059 | 0.83612 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 5003 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
34024010 |  |  | 3 | 40 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2079.9 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2080 | 3860 | 4229 | 5637 | 179 | 332 | 364 | 485 | 0.25728 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2311 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
34024011 |  |  | 3 | 40 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2063.12 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2063 | 5238 | 5738 | 7648 | 177 | 450 | 493 | 658 | 0.4547 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 3034 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
34024015 |  |  | 3 | 40 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3010.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3010 | 4730 | 4902 | 7188 | 259 | 407 | 422 | 618 | 0.4369 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 3763 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
34024016 |  |  | 3 | 40 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 2774.4 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2774 | 6916 | 7168 | 10512 | 239 | 595 | 616 | 904 | 1.0118 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 4080 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
34024020 |  |  | 3 | 40 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4216 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4216 | 6176 | 6766 | 9018 | 363 | 531 | 582 | 776 | 0.63066 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 5270 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
34024021 |  |  | 3 | 40 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4366.4 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4366 | 8907 | 9231 | 13538 | 375 | 766 | 794 | 1164 | 1.0139 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 5458 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
34026010 |  |  | 3 | 40 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2253.6 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2254 | 4178 | 4608 | 6144 | 194 | 359 | 396 | 528 | 0.31315 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2504 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
34026011 |  |  | 3 | 40 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2234.48 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2234 | 5669 | 6253 | 8337 | 192 | 488 | 538 | 717 | 0.55646 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3286 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
34026015 |  |  | 3 | 40 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3261.6 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3262 | 4942 | 5122 | 7511 | 281 | 425 | 440 | 646 | 0.52438 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4077 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
34026016 |  |  | 3 | 40 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3005.6 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3006 | 7342 | 7610 | 11159 | 259 | 631 | 654 | 960 | 1.2058 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 4420 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
34026020 |  |  | 3 | 40 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4568 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4568 | 6445 | 7108 | 9477 | 393 | 554 | 611 | 815 | 0.75018 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 5710 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
34026021 |  |  | 3 | 40 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4729.6 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4730 | 9235 | 9571 | 14035 | 407 | 794 | 823 | 1207 | 1.2174 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 5912 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
34028010 |  |  | 3 | 40 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2426.4 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2426 | 4331 | 4782 | 6370 | 209 | 372 | 411 | 548 | 0.37587 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 2696 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
34028011 |  |  | 3 | 40 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2406.52 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2407 | 5977 | 6599 | 8790 | 207 | 514 | 568 | 756 | 0.67116 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3539 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
34028015 |  |  | 3 | 40 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3512 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3512 | 5584 | 5709 | 8484 | 302 | 480 | 491 | 730 | 0.61729 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4390 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
34028016 |  |  | 3 | 40 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3236.8 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3237 | 8166 | 8348 | 12406 | 278 | 702 | 718 | 1067 | 1.4095 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 4760 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
34028020 |  |  | 3 | 40 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 4919.2 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 4919 | 7237 | 7990 | 10642 | 423 | 622 | 687 | 915 | 0.88151 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 6149 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
34028021 |  |  | 3 | 40 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5093.6 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 5094 | 10516 | 10751 | 15977 | 438 | 904 | 925 | 1374 | 1.4363 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 6367 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
34030010 |  |  | 3 | 40 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2600.1 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 2600 | 4485 | 4951 | 6595 | 224 | 386 | 426 | 567 | 0.44575 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 2889 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
34030011 |  |  | 3 | 40 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2578.56 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 2579 | 6285 | 6939 | 9242 | 222 | 541 | 597 | 795 | 0.79942 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 0.95 | 0.95 | 0.95 | 963 | 1063 | 1416 | 414 | 457 | 609 | 2.5034 | 3.0019 | 5.0929 | 4 | 16.2 | 18.6 | 31.4 |  | 3792 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 963 | 1063 | 1416 |  | 0 | 0 | 0 | 1
34030015 |  |  | 3 | 40 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3763.2 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 3763 | 5796 | 5926 | 8806 | 324 | 498 | 510 | 757 | 0.72336 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 4704 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
34030016 |  |  | 3 | 40 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3468 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 3468 | 8592 | 8784 | 13053 | 298 | 739 | 755 | 1123 | 1.6419 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 0.95 | 0.95 | 0.95 | 1260 | 1288 | 1915 | 542 | 554 | 823 | 5.2152 | 5.441 | 11.7219 | 6 | 19.3 | 20.4 | 34.5 |  | 5100 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1260 | 1288 | 1915 |  | 0 | 0 | 0 | 1
34030020 |  |  | 3 | 40 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5270.4 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 5270 | 7549 | 8335 | 11102 | 453 | 649 | 717 | 955 | 1.0249 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 6588 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
34030021 |  |  | 3 | 40 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5457.6 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 5458 | 10844 | 11086 | 16475 | 469 | 933 | 953 | 1417 | 1.6765 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 0.85 | 0.85 | 0.85 | 1468 | 1501 | 2231 | 631 | 645 | 959 | 2.9532 | 3.0797 | 6.5811 | 8 | 19.3 | 20.4 | 34.5 |  | 6822 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1468 | 1501 | 2231 |  | 0 | 0 | 0 | 1
3505010 |  |  | 3 | 50 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 484.2 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 484 | 649 | 695 | 812 | 42 | 56 | 60 | 70 | 0.0081621 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 538 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3505011 |  |  | 3 | 50 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 471.24 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 471 | 881 | 943 | 1102 | 41 | 76 | 81 | 95 | 0.012936 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 147.5614 | 157.9017 | 184.64 | 0.95 | 0.95 | 0.95 | 148 | 158 | 185 | 64 | 68 | 80 | 0.030576 | 0.034382 | 0.047099 | 0.7 | 3.6 | 4.1 | 5.1 |  | 693 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 148 | 158 | 185 |  | 0 | 0 | 0 | 1
3506010 |  |  | 3 | 50 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 581.4 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 581 | 842 | 901 | 1066 | 50 | 72 | 77 | 92 | 0.01214 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 646 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3506011 |  |  | 3 | 50 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 565.76 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 566 | 1142 | 1223 | 1447 | 49 | 98 | 105 | 124 | 0.019577 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 191 | 205 | 242 | 0.95 | 0.95 | 0.95 | 191 | 205 | 242 | 82 | 88 | 104 | 0.052655 | 0.060326 | 0.083243 | 0.8 | 4.8 | 5.4 | 6.8 |  | 832 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 191 | 205 | 242 |  | 0 | 0 | 0 | 1
3506015 |  |  | 3 | 50 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 832 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 832 | 957 | 1028 | 1360 | 72 | 82 | 88 | 117 | 0.026427 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1040 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3506016 |  |  | 3 | 50 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 774.52 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 775 | 1400 | 1503 | 1989 | 67 | 120 | 129 | 171 | 0.066509 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 214 | 230 | 305 | 0.95 | 0.95 | 0.95 | 214 | 230 | 305 | 92 | 99 | 131 | 0.12458 | 0.14404 | 0.25088 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1139 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 214 | 230 | 305 |  | 0 | 0 | 0 | 1
3506020 |  |  | 3 | 50 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1164 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1164 | 1347 | 1442 | 1706 | 100 | 116 | 124 | 147 | 0.040077 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1455 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3506021 |  |  | 3 | 50 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1239.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1239 | 1803 | 1935 | 2561 | 107 | 155 | 166 | 220 | 0.064814 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 233.8293 | 251.0106 | 332.22 | 0.85 | 0.85 | 0.85 | 234 | 251 | 332 | 101 | 108 | 143 | 0.057851 | 0.066012 | 0.11478 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1549 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 332 |  | 0 | 0 | 0 | 1
3507010 |  |  | 3 | 50 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 677.7 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 678 | 1030 | 1104 | 1320 | 58 | 89 | 95 | 114 | 0.017063 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 753 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3507011 |  |  | 3 | 50 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 659.6 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 660 | 1397 | 1498 | 1791 | 57 | 120 | 129 | 154 | 0.027897 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 234.0135 | 250.9543 | 300.04 | 0.95 | 0.95 | 0.95 | 234 | 251 | 300 | 101 | 108 | 129 | 0.083338 | 0.094767 | 0.13329 | 0.9 | 5.5 | 5.9 | 7.9 |  | 970 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 234 | 251 | 300 |  | 0 | 0 | 0 | 1
3507015 |  |  | 3 | 50 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1214 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3507016 |  |  | 3 | 50 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 903.72 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 904 | 1628 | 1747 | 2313 | 78 | 140 | 150 | 199 | 0.091342 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 219.5977 | 235.7333 | 312 | 0.95 | 0.95 | 0.95 | 220 | 236 | 312 | 95 | 101 | 134 | 0.13484 | 0.15219 | 0.26618 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1329 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 220 | 236 | 312 |  | 0 | 0 | 0 | 1
3507020 |  |  | 3 | 50 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1358.4 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1358 | 1510 | 1619 | 1936 | 117 | 130 | 139 | 166 | 0.055586 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1698 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3507021 |  |  | 3 | 50 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1445.6 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1446 | 1978 | 2123 | 2810 | 124 | 170 | 183 | 242 | 0.088673 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 240.3046 | 257.9617 | 341.42 | 0.85 | 0.85 | 0.85 | 240 | 258 | 341 | 103 | 111 | 147 | 0.061591 | 0.071336 | 0.12389 | 1.9 | 5.1 | 5.6 | 7.2 |  | 1807 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 341 |  | 0 | 0 | 0 | 1
3508010 |  |  | 3 | 50 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 774.9 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 775 | 1214 | 1304 | 1574 | 67 | 104 | 112 | 135 | 0.023665 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 861 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3508011 |  |  | 3 | 50 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 754.12 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 754 | 1648 | 1770 | 2136 | 65 | 142 | 152 | 184 | 0.03802 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12035 | 0.13629 | 0.19706 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1109 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
3508015 |  |  | 3 | 50 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1109.6 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1110 | 1395 | 1496 | 2008 | 95 | 120 | 129 | 173 | 0.047724 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1387 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3508016 |  |  | 3 | 50 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1032.24 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1032 | 2040 | 2188 | 2936 | 89 | 175 | 188 | 252 | 0.12041 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.26998 | 0.31121 | 0.56081 | 1.6 | 6 | 6.7 | 9 |  | 1518 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
3508020 |  |  | 3 | 50 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1552 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1552 | 1943 | 2086 | 2518 | 133 | 167 | 179 | 217 | 0.072735 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 1940 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3508021 |  |  | 3 | 50 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1652.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1653 | 2628 | 2818 | 3781 | 142 | 226 | 242 | 325 | 0.11828 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 340.8622 | 365.5154 | 490.42 | 0.85 | 0.85 | 0.85 | 341 | 366 | 490 | 147 | 157 | 211 | 0.12659 | 0.14403 | 0.25733 | 2.1 | 6 | 6.7 | 9 |  | 2066 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 341 | 366 | 490 |  | 0 | 0 | 0 | 1
3509010 |  |  | 3 | 50 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 871.2 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 871 | 1396 | 1501 | 1828 | 75 | 120 | 129 | 157 | 0.030768 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 968 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3509011 |  |  | 3 | 50 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 847.96 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 848 | 1894 | 2037 | 2480 | 73 | 163 | 175 | 213 | 0.050065 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 317.163 | 341.1777 | 415.44 | 0.95 | 0.95 | 0.95 | 317 | 341 | 415 | 136 | 147 | 178 | 0.16316 | 0.18921 | 0.27252 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1247 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 317 | 341 | 415 |  | 0 | 0 | 0 | 1
3509015 |  |  | 3 | 50 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1248.8 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1249 | 1598 | 1712 | 2331 | 107 | 137 | 147 | 200 | 0.061548 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1561 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3509016 |  |  | 3 | 50 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1161.44 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1161 | 2337 | 2503 | 3409 | 100 | 201 | 215 | 293 | 0.15381 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 357.7794 | 383.3036 | 522 | 0.95 | 0.95 | 0.95 | 358 | 383 | 522 | 154 | 165 | 224 | 0.36017 | 0.41267 | 0.75443 | 1.8 | 7 | 7.7 | 10.7 |  | 1708 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 358 | 383 | 522 |  | 0 | 0 | 0 | 1
3509020 |  |  | 3 | 50 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1746.4 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1746 | 2233 | 2402 | 2925 | 150 | 192 | 207 | 252 | 0.093602 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2183 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3509021 |  |  | 3 | 50 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 1859.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 1859 | 3009 | 3224 | 4391 | 160 | 259 | 277 | 378 | 0.1526 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 390.3496 | 418.1974 | 569.52 | 0.85 | 0.85 | 0.85 | 390 | 418 | 570 | 168 | 180 | 245 | 0.1679 | 0.19218 | 0.35163 | 2.4 | 7 | 7.7 | 10.7 |  | 2324 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 390 | 418 | 570 |  | 0 | 0 | 0 | 1
35010010 |  |  | 3 | 50 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 968.4 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 968 | 1574 | 1696 | 2082 | 83 | 135 | 146 | 179 | 0.038999 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1076 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
35010011 |  |  | 3 | 50 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 942.48 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 942 | 2136 | 2301 | 2825 | 81 | 184 | 198 | 243 | 0.064146 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21644 | 0.24959 | 0.3659 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1386 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
35010015 |  |  | 3 | 50 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1387.2 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1387 | 1799 | 1926 | 2655 | 119 | 155 | 166 | 228 | 0.077325 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1734 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
35010016 |  |  | 3 | 50 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1290.64 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1291 | 2630 | 2817 | 3883 | 111 | 226 | 242 | 334 | 0.19165 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45896 | 0.52378 | 0.99367 | 2 | 7 | 7.7 | 10.7 |  | 1898 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
35010020 |  |  | 3 | 50 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 1940 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1940 | 2519 | 2714 | 3331 | 167 | 217 | 233 | 286 | 0.11732 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2425 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
35010021 |  |  | 3 | 50 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2065.6 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2066 | 3388 | 3627 | 5000 | 178 | 291 | 312 | 430 | 0.19177 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 439.4163 | 470.5178 | 648.62 | 0.85 | 0.85 | 0.85 | 439 | 471 | 649 | 189 | 203 | 279 | 0.2156 | 0.24792 | 0.46187 | 2.7 | 7 | 7.7 | 10.7 |  | 2582 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 439 | 471 | 649 |  | 0 | 0 | 0 | 1
35011010 |  |  | 3 | 50 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1065.6 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1066 | 1766 | 1903 | 2336 | 92 | 152 | 164 | 201 | 0.049428 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1184 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
35011011 |  |  | 3 | 50 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1037 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1037 | 2397 | 2582 | 3169 | 89 | 206 | 222 | 273 | 0.080376 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 401.4205 | 432.4594 | 530.84 | 0.95 | 0.95 | 0.95 | 401 | 432 | 531 | 172 | 186 | 228 | 0.27875 | 0.32327 | 0.47559 | 1.5 | 8.4 | 9.3 | 14 |  | 1525 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 401 | 432 | 531 |  | 0 | 0 | 0 | 1
35011015 |  |  | 3 | 50 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1525.6 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1526 | 1908 | 2043 | 2817 | 131 | 164 | 176 | 242 | 0.095111 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 1907 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
35011016 |  |  | 3 | 50 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1419.84 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1420 | 2850 | 3051 | 4207 | 122 | 245 | 262 | 362 | 0.23401 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 407.833 | 436.699 | 602 | 0.95 | 0.95 | 0.95 | 408 | 437 | 602 | 175 | 188 | 259 | 0.47548 | 0.54745 | 1.0286 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2088 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 408 | 437 | 602 |  | 0 | 0 | 0 | 1
35011020 |  |  | 3 | 50 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2134.4 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2134 | 2693 | 2901 | 3561 | 184 | 232 | 249 | 306 | 0.14394 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2668 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
35011021 |  |  | 3 | 50 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2272 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2272 | 3556 | 3808 | 5249 | 195 | 306 | 327 | 451 | 0.23357 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 445.649 | 477.1916 | 657.82 | 0.85 | 0.85 | 0.85 | 446 | 477 | 658 | 192 | 205 | 283 | 0.22662 | 0.2575 | 0.48326 | 2.9 | 7.9 | 8.8 | 12.5 |  | 2840 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 446 | 477 | 658 |  | 0 | 0 | 0 | 1
35012010 |  |  | 3 | 50 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1161.9 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1162 | 1925 | 2080 | 2590 | 100 | 166 | 179 | 223 | 0.060199 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1291 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
35012011 |  |  | 3 | 50 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1130.84 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1131 | 2612 | 2822 | 3514 | 97 | 225 | 243 | 302 | 0.098862 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34359 | 0.3972 | 0.60239 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1663 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
35012015 |  |  | 3 | 50 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1664.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1665 | 2217 | 2374 | 3303 | 143 | 191 | 204 | 284 | 0.11496 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2081 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
35012016 |  |  | 3 | 50 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1549.04 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1549 | 3242 | 3472 | 4830 | 133 | 279 | 299 | 415 | 0.281 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70834 | 0.81671 | 1.558 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2278 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
35012020 |  |  | 3 | 50 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2328 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2328 | 3080 | 3327 | 4143 | 200 | 265 | 286 | 356 | 0.17184 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 2910 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
35012021 |  |  | 3 | 50 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2478.4 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2478 | 4175 | 4471 | 6220 | 213 | 359 | 385 | 535 | 0.28258 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 541.5608 | 579.9351 | 806.82 | 0.85 | 0.85 | 0.85 | 542 | 580 | 807 | 233 | 249 | 347 | 0.33654 | 0.38304 | 0.73179 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3098 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 542 | 580 | 807 |  | 0 | 0 | 0 | 1
35014010 |  |  | 3 | 50 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1355.4 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1355 | 2268 | 2456 | 3098 | 117 | 195 | 211 | 266 | 0.087073 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1506 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
35014011 |  |  | 3 | 50 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1319.2 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1319 | 3077 | 3333 | 4203 | 113 | 265 | 287 | 361 | 0.14302 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50267 | 0.587 | 0.9105 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1940 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
35014015 |  |  | 3 | 50 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 1942.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1942 | 2629 | 2815 | 3950 | 167 | 226 | 242 | 340 | 0.16105 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2428 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
35014016 |  |  | 3 | 50 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1806.76 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1807 | 3844 | 4117 | 5777 | 155 | 331 | 354 | 497 | 0.38918 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0162 | 1.1629 | 2.2701 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2657 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
35014020 |  |  | 3 | 50 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2716 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2716 | 3628 | 3929 | 4956 | 234 | 312 | 338 | 426 | 0.23982 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3395 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
35014021 |  |  | 3 | 50 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 2892 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2892 | 4951 | 5302 | 7440 | 249 | 426 | 456 | 640 | 0.39641 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 642.2257 | 687.7788 | 965.02 | 0.85 | 0.85 | 0.85 | 642 | 688 | 965 | 276 | 296 | 415 | 0.48412 | 0.55461 | 1.0702 | 3.7 | 9.6 | 10.5 | 16.1 |  | 3615 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 642 | 688 | 965 |  | 0 | 0 | 0 | 1
35016010 |  |  | 3 | 50 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1549.8 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1550 | 2604 | 2827 | 3605 | 133 | 224 | 243 | 310 | 0.1184 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1722 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
35016011 |  |  | 3 | 50 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1508.24 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1508 | 3533 | 3835 | 4892 | 130 | 304 | 330 | 421 | 0.2003 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592 | 642 | 819 | 0.95 | 0.95 | 0.95 | 592 | 642 | 819 | 255 | 276 | 352 | 0.70443 | 0.81699 | 1.2894 | 2.1 | 11 | 12.4 | 19.2 |  | 2218 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 592 | 642 | 819 |  | 0 | 0 | 0 | 1
35016015 |  |  | 3 | 50 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2219.2 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2219 | 3021 | 3226 | 4598 | 191 | 260 | 277 | 395 | 0.216 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2774 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
35016016 |  |  | 3 | 50 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2065.16 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2065 | 4418 | 4717 | 6724 | 178 | 380 | 406 | 578 | 0.5226 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 676 | 722 | 1030 | 0.95 | 0.95 | 0.95 | 676 | 722 | 1030 | 291 | 310 | 443 | 1.3662 | 1.5463 | 3.1127 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3037 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 676 | 722 | 1030 |  | 0 | 0 | 0 | 1
35016020 |  |  | 3 | 50 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3104 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3104 | 4166 | 4522 | 5768 | 267 | 358 | 389 | 496 | 0.318 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 3880 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
35016021 |  |  | 3 | 50 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3304.8 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3305 | 5690 | 6075 | 8659 | 284 | 489 | 522 | 745 | 0.52853 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 738.0334 | 787.9738 | 1123.22 | 0.85 | 0.85 | 0.85 | 738 | 788 | 1123 | 317 | 339 | 483 | 0.65391 | 0.7447 | 1.4802 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4131 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 738 | 788 | 1123 |  | 0 | 0 | 0 | 1
35018010 |  |  | 3 | 50 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1743.3 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1743 | 2971 | 3225 | 4113 | 150 | 256 | 277 | 354 | 0.15767 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 1937 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
35018011 |  |  | 3 | 50 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1696.6 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1697 | 4031 | 4376 | 5581 | 146 | 347 | 376 | 480 | 0.26629 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675.1031 | 732.8571 | 934.74 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.95449 | 1.1138 | 1.7574 | 2.4 | 12.2 | 13.7 | 22 |  | 2495 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
35018015 |  |  | 3 | 50 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2496.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2497 | 3233 | 3452 | 4921 | 215 | 278 | 297 | 423 | 0.28019 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3121 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
35018016 |  |  | 3 | 50 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2322.88 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2323 | 4843 | 5171 | 7371 | 200 | 417 | 445 | 634 | 0.67129 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686.3089 | 732.7493 | 1044.5 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4328 | 1.6286 | 3.257 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3416 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
35018020 |  |  | 3 | 50 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3492 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3492 | 4498 | 4883 | 6228 | 300 | 387 | 420 | 536 | 0.40847 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4365 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
35018021 |  |  | 3 | 50 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3718.4 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3718 | 6017 | 6424 | 9157 | 320 | 517 | 552 | 788 | 0.68655 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 750.1235 | 800.882 | 1141.62 | 0.85 | 0.85 | 0.85 | 750 | 801 | 1142 | 323 | 344 | 491 | 0.69903 | 0.78947 | 1.5713 | 4.8 | 11.5 | 12.8 | 19.6 |  | 4648 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 750 | 801 | 1142 |  | 0 | 0 | 0 | 1
35020010 |  |  | 3 | 50 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 1936.8 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1937 | 3260 | 3553 | 4621 | 167 | 280 | 306 | 397 | 0.20392 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2152 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
35020011 |  |  | 3 | 50 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 1884.96 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1885 | 4423 | 4821 | 6270 | 162 | 380 | 415 | 539 | 0.34411 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 741 | 807 | 1050 | 0.95 | 0.95 | 0.95 | 741 | 807 | 1050 | 319 | 347 | 452 | 1.209 | 1.4139 | 2.3144 | 2.7 | 13.4 | 14.8 | 24 |  | 2772 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 741 | 807 | 1050 |  | 0 | 0 | 0 | 1
35020015 |  |  | 3 | 50 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2774.4 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2774 | 3875 | 4083 | 5893 | 239 | 333 | 351 | 507 | 0.354 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3468 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
35020016 |  |  | 3 | 50 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2581.28 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2581 | 5667 | 5971 | 8618 | 222 | 487 | 514 | 741 | 0.84084 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 868 | 914 | 1320 | 0.95 | 0.95 | 0.95 | 868 | 914 | 1320 | 373 | 393 | 568 | 2.3103 | 2.5582 | 5.2529 | 4 | 13.2 | 14.7 | 23.5 |  | 3796 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 868 | 914 | 1320 |  | 0 | 0 | 0 | 1
35020020 |  |  | 3 | 50 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 3880 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 3880 | 5215 | 5684 | 7393 | 334 | 448 | 489 | 636 | 0.51461 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 4850 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
35020021 |  |  | 3 | 50 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4131.2 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4131 | 7299 | 7690 | 11098 | 355 | 628 | 661 | 954 | 0.8636 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 946.7235 | 997.5379 | 1439.62 | 0.85 | 0.85 | 0.85 | 947 | 998 | 1440 | 407 | 429 | 619 | 1.1239 | 1.244 | 2.5261 | 5.3 | 13.2 | 14.7 | 23.5 |  | 5164 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 947 | 998 | 1440 |  | 0 | 0 | 0 | 1
35022010 |  |  | 3 | 50 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2130.3 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2130 | 3561 | 3891 | 5129 | 183 | 306 | 335 | 441 | 0.25496 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2367 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
35022011 |  |  | 3 | 50 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2073.32 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2073 | 4831 | 5279 | 6959 | 178 | 415 | 454 | 598 | 0.43451 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 809.1873 | 884.1366 | 1165.54 | 0.95 | 0.95 | 0.95 | 809 | 884 | 1166 | 348 | 380 | 501 | 1.5012 | 1.7674 | 2.9548 | 2.9 | 13.4 | 14.8 | 24 |  | 3049 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 809 | 884 | 1166 |  | 0 | 0 | 0 | 1
35022015 |  |  | 3 | 50 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3052 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3052 | 4303 | 4482 | 6541 | 262 | 370 | 385 | 563 | 0.43459 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 3815 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
35022016 |  |  | 3 | 50 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 2839.68 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2840 | 6292 | 6554 | 9565 | 244 | 541 | 564 | 823 | 1.0318 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 963.3581 | 1003.4911 | 1464.5 | 0.95 | 0.95 | 0.95 | 963 | 1003 | 1465 | 414 | 431 | 630 | 2.8848 | 3.1201 | 6.5422 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4176 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 963 | 1003 | 1465 |  | 0 | 0 | 0 | 1
35022020 |  |  | 3 | 50 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4268 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4268 | 5697 | 6224 | 8205 | 367 | 490 | 535 | 706 | 0.63115 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 5335 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
35022021 |  |  | 3 | 50 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 4544 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4544 | 8103 | 8440 | 12318 | 391 | 697 | 726 | 1059 | 1.0694 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1051.0569 | 1094.8434 | 1597.82 | 0.85 | 0.85 | 0.85 | 1051 | 1095 | 1598 | 452 | 471 | 687 | 1.4133 | 1.5298 | 3.1674 | 5.9 | 15.5 | 16.8 | 27.5 |  | 5680 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 1051 | 1095 | 1598 |  | 0 | 0 | 0 | 1
35024010 |  |  | 3 | 50 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2323.8 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2324 | 3860 | 4229 | 5637 | 200 | 332 | 364 | 485 | 0.31605 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2582 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
35024011 |  |  | 3 | 50 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2261.68 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2262 | 5238 | 5738 | 7648 | 195 | 450 | 493 | 658 | 0.54331 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8332 | 2.1704 | 3.7044 | 3.2 | 14.8 | 16.6 | 28 |  | 3326 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
35024015 |  |  | 3 | 50 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3329.6 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3330 | 4730 | 4902 | 7188 | 286 | 407 | 422 | 618 | 0.52835 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4162 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
35024016 |  |  | 3 | 50 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3097.4 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3097 | 6916 | 7168 | 10512 | 266 | 595 | 616 | 904 | 1.2449 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.53 | 3.7911 | 7.9872 | 4.8 | 16.4 | 17.7 | 29.7 |  | 4555 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
35024020 |  |  | 3 | 50 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 4656 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4656 | 6176 | 6766 | 9018 | 400 | 531 | 582 | 776 | 0.76111 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 5820 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
35024021 |  |  | 3 | 50 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 4957.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4958 | 8907 | 9231 | 13538 | 426 | 766 | 794 | 1164 | 1.2947 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1155.406 | 1197.4378 | 1756.02 | 0.85 | 0.85 | 0.85 | 1155 | 1197 | 1756 | 497 | 515 | 755 | 1.7405 | 1.8637 | 3.8911 | 6.4 | 16.4 | 17.7 | 29.7 |  | 6197 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1155 | 1197 | 1756 |  | 0 | 0 | 0 | 1
35026010 |  |  | 3 | 50 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2518.2 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2518 | 4178 | 4608 | 6144 | 217 | 359 | 396 | 528 | 0.38529 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 2798 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
35026011 |  |  | 3 | 50 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2450.72 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2451 | 5669 | 6253 | 8337 | 211 | 488 | 538 | 717 | 0.66162 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 949.5112 | 1047.255 | 1396.34 | 0.95 | 0.95 | 0.95 | 950 | 1047 | 1396 | 409 | 450 | 600 | 2.2371 | 2.6689 | 4.5448 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3604 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 950 | 1047 | 1396 |  | 0 | 0 | 0 | 1
35026015 |  |  | 3 | 50 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3606.4 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3606 | 4942 | 5122 | 7511 | 310 | 425 | 440 | 646 | 0.63277 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4508 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
35026016 |  |  | 3 | 50 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3355.8 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3356 | 7342 | 7610 | 11159 | 289 | 631 | 654 | 960 | 1.4906 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1068.87 | 1107.7539 | 1624.5 | 0.95 | 0.95 | 0.95 | 1069 | 1108 | 1625 | 460 | 476 | 699 | 3.6695 | 3.9213 | 8.2764 | 5.2 | 16.4 | 17.7 | 29.7 |  | 4935 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1069 | 1108 | 1625 |  | 0 | 0 | 0 | 1
35026020 |  |  | 3 | 50 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5044 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 5044 | 6445 | 7108 | 9477 | 434 | 554 | 611 | 815 | 0.90889 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 6305 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
35026021 |  |  | 3 | 50 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5370.4 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5370 | 9235 | 9571 | 14035 | 462 | 794 | 823 | 1207 | 1.5516 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1167.5127 | 1209.985 | 1774.42 | 0.85 | 0.85 | 0.85 | 1168 | 1210 | 1774 | 502 | 520 | 763 | 1.8191 | 1.9461 | 4.0629 | 6.9 | 16.4 | 17.7 | 29.7 |  | 6713 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1168 | 1210 | 1774 |  | 0 | 0 | 0 | 1
35028010 |  |  | 3 | 50 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2711.7 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2712 | 4331 | 4782 | 6370 | 233 | 372 | 411 | 548 | 0.45943 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3013 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
35028011 |  |  | 3 | 50 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2639.08 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2639 | 5977 | 6599 | 8790 | 227 | 514 | 568 | 756 | 0.79462 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 956 | 1056 | 1406 | 0.95 | 0.95 | 0.95 | 956 | 1056 | 1406 | 411 | 454 | 605 | 2.3638 | 2.8393 | 4.8233 | 3.7 | 16.2 | 18.6 | 31.4 |  | 3881 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 956 | 1056 | 1406 |  | 0 | 0 | 0 | 1
35028015 |  |  | 3 | 50 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 3884 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 3884 | 5584 | 5709 | 8484 | 334 | 480 | 491 | 730 | 0.74818 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 4855 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
35028016 |  |  | 3 | 50 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3613.52 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3614 | 8166 | 8348 | 12406 | 311 | 702 | 718 | 1067 | 1.7504 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1250 | 1278 | 1900 | 0.95 | 0.95 | 0.95 | 1250 | 1278 | 1900 | 538 | 550 | 817 | 5.0575 | 5.2787 | 11.3853 | 5.6 | 19.3 | 20.4 | 34.5 |  | 5314 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1250 | 1278 | 1900 |  | 0 | 0 | 0 | 1
35028020 |  |  | 3 | 50 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5432 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 5432 | 7237 | 7990 | 10642 | 467 | 622 | 687 | 915 | 1.0671 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 6790 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
35028021 |  |  | 3 | 50 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5784 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 5784 | 10516 | 10751 | 15977 | 497 | 904 | 925 | 1374 | 1.8285 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1261.7809 | 1290.0229 | 1916.9885 | 0.85 | 0.85 | 0.85 | 1262 | 1290 | 1917 | 543 | 555 | 824 | 2.1656 | 2.2581 | 4.8156 | 7.5 | 19.3 | 20.4 | 34.5 |  | 7230 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1262 | 1290 | 1917 |  | 0 | 0 | 0 | 1
35030010 |  |  | 3 | 50 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2905.2 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 2905 | 4485 | 4951 | 6595 | 250 | 386 | 426 | 567 | 0.54575 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 3228 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
35030011 |  |  | 3 | 50 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2827.44 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 2827 | 6285 | 6939 | 9242 | 243 | 541 | 597 | 795 | 0.94299 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 963 | 1063 | 1416 | 0.95 | 0.95 | 0.95 | 963 | 1063 | 1416 | 414 | 457 | 609 | 2.5034 | 3.0019 | 5.0929 | 4 | 16.2 | 18.6 | 31.4 |  | 4158 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 963 | 1063 | 1416 |  | 0 | 0 | 0 | 1
35030015 |  |  | 3 | 50 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4161.6 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 4162 | 5796 | 5926 | 8806 | 358 | 498 | 510 | 757 | 0.87491 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 5202 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
35030016 |  |  | 3 | 50 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3871.92 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 3872 | 8592 | 8784 | 13053 | 333 | 739 | 755 | 1123 | 2.0341 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1260 | 1288 | 1915 | 0.95 | 0.95 | 0.95 | 1260 | 1288 | 1915 | 542 | 554 | 823 | 5.2152 | 5.441 | 11.7219 | 6 | 19.3 | 20.4 | 34.5 |  | 5694 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1260 | 1288 | 1915 |  | 0 | 0 | 0 | 1
35030020 |  |  | 3 | 50 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5820 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 5820 | 7549 | 8335 | 11102 | 501 | 649 | 717 | 955 | 1.2446 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 7275 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
35030021 |  |  | 3 | 50 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6196.8 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 6197 | 10844 | 11086 | 16475 | 533 | 933 | 953 | 1417 | 2.1396 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1468 | 1501 | 2231 | 0.85 | 0.85 | 0.85 | 1468 | 1501 | 2231 | 631 | 645 | 959 | 2.9532 | 3.0797 | 6.5811 | 8 | 19.3 | 20.4 | 34.5 |  | 7746 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1468 | 1501 | 2231 |  | 0 | 0 | 0 | 1
3605010 |  |  | 3 | 60 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 526.5 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 527 | 649 | 695 | 812 | 45 | 56 | 60 | 70 | 0.009332 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 585 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3605011 |  |  | 3 | 60 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 507.96 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 508 | 881 | 943 | 1102 | 44 | 76 | 81 | 95 | 0.014824 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 140.1833 | 150.0066 | 175.408 | 0.95 | 0.95 | 0.95 | 140 | 150 | 175 | 60 | 65 | 75 | 0.026988 | 0.031507 | 0.041564 | 0.7 | 3.6 | 4.1 | 5.1 |  | 747 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 140 | 150 | 175 |  | 0 | 0 | 0 | 1
3606010 |  |  | 3 | 60 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 631.8 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 632 | 842 | 901 | 1066 | 54 | 72 | 77 | 92 | 0.014086 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 702 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3606011 |  |  | 3 | 60 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 609.28 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 609 | 1142 | 1223 | 1447 | 52 | 98 | 105 | 124 | 0.02194 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 181.45 | 194.75 | 229.9 | 0.95 | 0.95 | 0.95 | 181 | 195 | 230 | 78 | 84 | 99 | 0.047823 | 0.055156 | 0.075698 | 0.8 | 4.8 | 5.4 | 6.8 |  | 896 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 181 | 195 | 230 |  | 0 | 0 | 0 | 1
3606015 |  |  | 3 | 60 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1120 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3606016 |  |  | 3 | 60 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 850 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 850 | 1400 | 1503 | 1989 | 73 | 120 | 129 | 171 | 0.078809 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 203.3 | 218.5 | 289.75 | 0.95 | 0.95 | 0.95 | 203 | 219 | 290 | 87 | 94 | 125 | 0.11153 | 0.12999 | 0.22862 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1250 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 203 | 219 | 290 |  | 0 | 0 | 0 | 1
3606020 |  |  | 3 | 60 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1565 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3606021 |  |  | 3 | 60 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1383.2 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1383 | 1803 | 1935 | 2561 | 119 | 155 | 166 | 220 | 0.07991 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 222.1379 | 238.4601 | 315.609 | 0.85 | 0.85 | 0.85 | 222 | 238 | 316 | 95 | 102 | 136 | 0.05128 | 0.058985 | 0.10397 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1729 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 222 | 238 | 316 |  | 0 | 0 | 0 | 1
3607010 |  |  | 3 | 60 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 737.1 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 737 | 1030 | 1104 | 1320 | 63 | 89 | 95 | 114 | 0.020005 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 819 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3607011 |  |  | 3 | 60 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 711.28 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 711 | 1397 | 1498 | 1791 | 61 | 120 | 129 | 154 | 0.031753 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 222.3128 | 238.4066 | 285.038 | 0.95 | 0.95 | 0.95 | 222 | 238 | 285 | 95 | 102 | 123 | 0.074106 | 0.084927 | 0.12164 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1046 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 222 | 238 | 285 |  | 0 | 0 | 0 | 1
3607015 |  |  | 3 | 60 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1306 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3607016 |  |  | 3 | 60 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 992.12 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 992 | 1628 | 1747 | 2313 | 85 | 140 | 150 | 199 | 0.10824 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 208.6178 | 223.9466 | 296.4 | 0.95 | 0.95 | 0.95 | 209 | 224 | 296 | 90 | 96 | 127 | 0.12118 | 0.13766 | 0.23938 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1459 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 209 | 224 | 296 |  | 0 | 0 | 0 | 1
3607020 |  |  | 3 | 60 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1826 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3607021 |  |  | 3 | 60 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1613.6 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1614 | 1978 | 2123 | 2810 | 139 | 170 | 183 | 242 | 0.11098 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 228.2894 | 245.0636 | 324.349 | 0.85 | 0.85 | 0.85 | 228 | 245 | 324 | 98 | 105 | 139 | 0.055859 | 0.063961 | 0.11098 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2017 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 228 | 245 | 324 |  | 0 | 0 | 0 | 1
3608010 |  |  | 3 | 60 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 842.4 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 842 | 1214 | 1304 | 1574 | 72 | 104 | 112 | 135 | 0.027165 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 936 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3608011 |  |  | 3 | 60 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 812.6 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 813 | 1648 | 1770 | 2136 | 70 | 142 | 152 | 184 | 0.043772 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 262.2 | 281.2 | 340.1 | 0.95 | 0.95 | 0.95 | 262 | 281 | 340 | 113 | 121 | 146 | 0.10903 | 0.12425 | 0.17793 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1195 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 262 | 281 | 340 |  | 0 | 0 | 0 | 1
3608015 |  |  | 3 | 60 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1194.4 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1194 | 1395 | 1496 | 2008 | 103 | 120 | 129 | 173 | 0.055922 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1493 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3608016 |  |  | 3 | 60 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1133.56 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1134 | 2040 | 2188 | 2936 | 98 | 175 | 188 | 252 | 0.1456 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 296.4 | 318.25 | 427.5 | 0.95 | 0.95 | 0.95 | 296 | 318 | 428 | 127 | 137 | 184 | 0.24284 | 0.28204 | 0.50511 | 1.6 | 6 | 6.7 | 9 |  | 1667 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 296 | 318 | 428 |  | 0 | 0 | 0 | 1
3608020 |  |  | 3 | 60 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1668.8 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1669 | 1943 | 2086 | 2518 | 144 | 167 | 179 | 217 | 0.085073 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2086 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3608021 |  |  | 3 | 60 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 1844.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 1845 | 2628 | 2818 | 3781 | 159 | 226 | 242 | 325 | 0.14765 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 323.8191 | 347.2396 | 465.899 | 0.85 | 0.85 | 0.85 | 324 | 347 | 466 | 139 | 149 | 200 | 0.11343 | 0.12999 | 0.23164 | 2.1 | 6 | 6.7 | 9 |  | 2306 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 324 | 347 | 466 |  | 0 | 0 | 0 | 1
3609010 |  |  | 3 | 60 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 947.7 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 948 | 1396 | 1501 | 1828 | 82 | 120 | 129 | 157 | 0.036485 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1053 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3609011 |  |  | 3 | 60 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 914.6 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 915 | 1894 | 2037 | 2480 | 79 | 163 | 175 | 213 | 0.058145 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 301.3049 | 324.1188 | 394.668 | 0.95 | 0.95 | 0.95 | 301 | 324 | 395 | 129 | 139 | 170 | 0.14755 | 0.17008 | 0.24963 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1345 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 301 | 324 | 395 |  | 0 | 0 | 0 | 1
3609015 |  |  | 3 | 60 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1343.2 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1343 | 1598 | 1712 | 2331 | 115 | 137 | 147 | 200 | 0.070874 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1679 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3609016 |  |  | 3 | 60 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1275.68 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1276 | 2337 | 2503 | 3409 | 110 | 201 | 215 | 293 | 0.18557 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 339.8904 | 364.1384 | 495.9 | 0.95 | 0.95 | 0.95 | 340 | 364 | 496 | 146 | 157 | 213 | 0.3242 | 0.37413 | 0.68303 | 1.8 | 7 | 7.7 | 10.7 |  | 1876 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 340 | 364 | 496 |  | 0 | 0 | 0 | 1
3609020 |  |  | 3 | 60 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1877.6 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1878 | 2233 | 2402 | 2925 | 162 | 192 | 207 | 252 | 0.10892 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2347 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3609021 |  |  | 3 | 60 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2075.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2075 | 3009 | 3224 | 4391 | 178 | 259 | 277 | 378 | 0.18802 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 370.8322 | 397.2875 | 541.044 | 0.85 | 0.85 | 0.85 | 371 | 397 | 541 | 160 | 171 | 233 | 0.1526 | 0.17381 | 0.31865 | 2.4 | 7 | 7.7 | 10.7 |  | 2594 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 371 | 397 | 541 |  | 0 | 0 | 0 | 1
36010010 |  |  | 3 | 60 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1053 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1053 | 1574 | 1696 | 2082 | 91 | 135 | 146 | 179 | 0.046467 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1170 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
36010011 |  |  | 3 | 60 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1015.92 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1016 | 2136 | 2301 | 2825 | 87 | 184 | 198 | 243 | 0.073411 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 340.1 | 365.75 | 449.35 | 0.95 | 0.95 | 0.95 | 340 | 366 | 449 | 146 | 157 | 193 | 0.1956 | 0.22452 | 0.33237 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1494 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 340 | 366 | 449 |  | 0 | 0 | 0 | 1
36010015 |  |  | 3 | 60 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1492.8 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1493 | 1799 | 1926 | 2655 | 128 | 155 | 166 | 228 | 0.089158 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1866 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
36010016 |  |  | 3 | 60 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1417.12 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1417 | 2630 | 2817 | 3883 | 122 | 226 | 242 | 334 | 0.23078 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 382.85 | 409.45 | 565.25 | 0.95 | 0.95 | 0.95 | 383 | 409 | 565 | 165 | 176 | 243 | 0.4181 | 0.47477 | 0.89661 | 2 | 7 | 7.7 | 10.7 |  | 2084 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 383 | 409 | 565 |  | 0 | 0 | 0 | 1
36010020 |  |  | 3 | 60 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2086.4 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2086 | 2519 | 2714 | 3331 | 179 | 217 | 233 | 286 | 0.13447 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2608 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
36010021 |  |  | 3 | 60 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2305.6 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2306 | 3388 | 3627 | 5000 | 198 | 291 | 312 | 430 | 0.23612 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 417.4455 | 446.9919 | 616.189 | 0.85 | 0.85 | 0.85 | 417 | 447 | 616 | 179 | 192 | 265 | 0.19388 | 0.22234 | 0.41758 | 2.7 | 7 | 7.7 | 10.7 |  | 2882 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 417 | 447 | 616 |  | 0 | 0 | 0 | 1
36011010 |  |  | 3 | 60 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1158.3 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1158 | 1766 | 1903 | 2336 | 100 | 152 | 164 | 201 | 0.057908 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1287 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
36011011 |  |  | 3 | 60 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1117.24 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1117 | 2397 | 2582 | 3169 | 96 | 206 | 222 | 273 | 0.092688 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 381.3495 | 410.8364 | 504.298 | 0.95 | 0.95 | 0.95 | 381 | 411 | 504 | 164 | 177 | 217 | 0.25472 | 0.29429 | 0.43299 | 1.5 | 8.4 | 9.3 | 14 |  | 1643 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 504 |  | 0 | 0 | 0 | 1
36011015 |  |  | 3 | 60 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1642.4 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1642 | 1908 | 2043 | 2817 | 141 | 164 | 176 | 242 | 0.10978 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2053 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
36011016 |  |  | 3 | 60 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1558.56 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1559 | 2850 | 3051 | 4207 | 134 | 245 | 262 | 362 | 0.28136 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 387.4413 | 414.864 | 571.9 | 0.95 | 0.95 | 0.95 | 387 | 415 | 572 | 166 | 178 | 246 | 0.42859 | 0.49165 | 0.92938 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2292 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 387 | 415 | 572 |  | 0 | 0 | 0 | 1
36011020 |  |  | 3 | 60 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2295.2 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2295 | 2693 | 2901 | 3561 | 197 | 232 | 249 | 306 | 0.16459 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 2869 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
36011021 |  |  | 3 | 60 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2536 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2536 | 3556 | 3808 | 5249 | 218 | 306 | 327 | 451 | 0.29032 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 423.3665 | 453.332 | 624.929 | 0.85 | 0.85 | 0.85 | 423 | 453 | 625 | 182 | 195 | 269 | 0.20417 | 0.23357 | 0.43765 | 2.9 | 7.9 | 8.8 | 12.5 |  | 3170 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 423 | 453 | 625 |  | 0 | 0 | 0 | 1
36012010 |  |  | 3 | 60 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1263.6 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1264 | 1925 | 2080 | 2590 | 109 | 166 | 179 | 223 | 0.070873 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1404 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
36012011 |  |  | 3 | 60 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1219.24 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1219 | 2612 | 2822 | 3514 | 105 | 225 | 243 | 302 | 0.11472 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 415.15 | 449.35 | 559.55 | 0.95 | 0.95 | 0.95 | 415 | 449 | 560 | 178 | 193 | 241 | 0.3099 | 0.36105 | 0.54946 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1793 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 415 | 449 | 560 |  | 0 | 0 | 0 | 1
36012015 |  |  | 3 | 60 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1791.2 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1791 | 2217 | 2374 | 3303 | 154 | 191 | 204 | 284 | 0.1328 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2239 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
36012016 |  |  | 3 | 60 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1700.68 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1701 | 3242 | 3472 | 4830 | 146 | 279 | 299 | 415 | 0.3374 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 471.2 | 505.4 | 703 | 0.95 | 0.95 | 0.95 | 471 | 505 | 703 | 203 | 217 | 302 | 0.64447 | 0.73472 | 1.4075 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2501 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 471 | 505 | 703 |  | 0 | 0 | 0 | 1
36012020 |  |  | 3 | 60 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2504 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2504 | 3080 | 3327 | 4143 | 215 | 265 | 286 | 356 | 0.19802 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3130 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
36012021 |  |  | 3 | 60 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 2766.4 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 2766 | 4175 | 4471 | 6220 | 238 | 359 | 385 | 535 | 0.35076 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 514.4827 | 550.9384 | 766.479 | 0.85 | 0.85 | 0.85 | 514 | 551 | 766 | 221 | 237 | 329 | 0.30361 | 0.34789 | 0.65951 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3458 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 514 | 551 | 766 |  | 0 | 0 | 0 | 1
36014010 |  |  | 3 | 60 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1474.2 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1474 | 2268 | 2456 | 3098 | 127 | 195 | 211 | 266 | 0.10163 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1638 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
36014011 |  |  | 3 | 60 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1422.56 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1423 | 3077 | 3333 | 4203 | 122 | 265 | 287 | 361 | 0.16504 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 489.25 | 530.1 | 668.8 | 0.95 | 0.95 | 0.95 | 489 | 530 | 669 | 210 | 228 | 288 | 0.45668 | 0.53302 | 0.82741 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2092 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 489 | 530 | 669 |  | 0 | 0 | 0 | 1
36014015 |  |  | 3 | 60 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2089.6 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2090 | 2629 | 2815 | 3950 | 180 | 226 | 242 | 340 | 0.18627 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2612 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
36014016 |  |  | 3 | 60 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 1984.24 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1984 | 3844 | 4117 | 5777 | 171 | 331 | 354 | 497 | 0.47167 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 559.55 | 598.5 | 840.75 | 0.95 | 0.95 | 0.95 | 560 | 599 | 841 | 241 | 258 | 362 | 0.92386 | 1.056 | 2.053 | 2.8 | 9.6 | 10.5 | 16.1 |  | 2918 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 560 | 599 | 841 |  | 0 | 0 | 0 | 1
36014020 |  |  | 3 | 60 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 2920.8 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2921 | 3628 | 3929 | 4956 | 251 | 312 | 338 | 426 | 0.27509 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3651 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
36014021 |  |  | 3 | 60 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3228 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3228 | 4951 | 5302 | 7440 | 278 | 426 | 456 | 640 | 0.49096 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 610.1144 | 653.3898 | 916.769 | 0.85 | 0.85 | 0.85 | 610 | 653 | 917 | 262 | 281 | 394 | 0.43757 | 0.50131 | 0.96732 | 3.7 | 9.6 | 10.5 | 16.1 |  | 4035 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 610 | 653 | 917 |  | 0 | 0 | 0 | 1
36016010 |  |  | 3 | 60 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1684.8 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1685 | 2604 | 2827 | 3605 | 145 | 224 | 243 | 310 | 0.13925 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1872 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
36016011 |  |  | 3 | 60 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1625.2 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1625 | 3533 | 3835 | 4892 | 140 | 304 | 330 | 421 | 0.22993 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 562.4 | 609.9 | 778.05 | 0.95 | 0.95 | 0.95 | 562 | 610 | 778 | 242 | 262 | 335 | 0.6387 | 0.74107 | 1.1749 | 2.1 | 11 | 12.4 | 19.2 |  | 2390 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 562 | 610 | 778 |  | 0 | 0 | 0 | 1
36016015 |  |  | 3 | 60 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2388.8 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2389 | 3021 | 3226 | 4598 | 205 | 260 | 277 | 395 | 0.24769 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 2986 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
36016016 |  |  | 3 | 60 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2267.12 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2267 | 4418 | 4717 | 6724 | 195 | 380 | 406 | 578 | 0.6245 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 642.2 | 685.9 | 978.5 | 0.95 | 0.95 | 0.95 | 642 | 686 | 979 | 276 | 295 | 421 | 1.2317 | 1.4032 | 2.8168 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3334 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 642 | 686 | 979 |  | 0 | 0 | 0 | 1
36016020 |  |  | 3 | 60 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3338.4 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3338 | 4166 | 4522 | 5768 | 287 | 358 | 389 | 496 | 0.36616 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 4173 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
36016021 |  |  | 3 | 60 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 3688.8 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 3689 | 5690 | 6075 | 8659 | 317 | 489 | 522 | 745 | 0.65391 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 701.1317 | 748.5751 | 1067.059 | 0.85 | 0.85 | 0.85 | 701 | 749 | 1067 | 301 | 322 | 459 | 0.59149 | 0.67404 | 1.3407 | 4.3 | 11.5 | 12.8 | 19.6 |  | 4611 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 701 | 749 | 1067 |  | 0 | 0 | 0 | 1
36018010 |  |  | 3 | 60 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 1895.4 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 1895 | 2971 | 3225 | 4113 | 163 | 256 | 277 | 354 | 0.18421 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 2106 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
36018011 |  |  | 3 | 60 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1828.52 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1829 | 4031 | 4376 | 5581 | 157 | 347 | 376 | 480 | 0.3047 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 641.348 | 696.2143 | 888.003 | 0.95 | 0.95 | 0.95 | 641 | 696 | 888 | 276 | 299 | 382 | 0.87032 | 1.0105 | 1.5973 | 2.4 | 12.2 | 13.7 | 22 |  | 2689 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 641 | 696 | 888 |  | 0 | 0 | 0 | 1
36018015 |  |  | 3 | 60 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2687.2 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2687 | 3233 | 3452 | 4921 | 231 | 278 | 297 | 423 | 0.32184 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3359 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
36018016 |  |  | 3 | 60 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2550.68 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2551 | 4843 | 5171 | 7371 | 219 | 417 | 445 | 634 | 0.80118 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 651.9934 | 696.1118 | 992.275 | 0.95 | 0.95 | 0.95 | 652 | 696 | 992 | 280 | 299 | 427 | 1.294 | 1.4709 | 2.952 | 3.6 | 11.5 | 12.8 | 19.6 |  | 3751 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 652 | 696 | 992 |  | 0 | 0 | 0 | 1
36018020 |  |  | 3 | 60 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3755.2 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3755 | 4498 | 4883 | 6228 | 323 | 387 | 420 | 536 | 0.47171 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4694 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
36018021 |  |  | 3 | 60 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4150.4 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4150 | 6017 | 6424 | 9157 | 357 | 517 | 552 | 788 | 0.84813 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 712.6173 | 760.8379 | 1084.539 | 0.85 | 0.85 | 0.85 | 713 | 761 | 1085 | 307 | 327 | 467 | 0.63372 | 0.71584 | 1.4259 | 4.8 | 11.5 | 12.8 | 19.6 |  | 5188 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 713 | 761 | 1085 |  | 0 | 0 | 0 | 1
36020010 |  |  | 3 | 60 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2106 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 2106 | 3260 | 3553 | 4621 | 181 | 280 | 306 | 397 | 0.23698 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2340 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
36020011 |  |  | 3 | 60 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2031.84 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2032 | 4423 | 4821 | 6270 | 175 | 380 | 415 | 539 | 0.39691 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 703.95 | 766.65 | 997.5 | 0.95 | 0.95 | 0.95 | 704 | 767 | 998 | 303 | 330 | 429 | 1.0986 | 1.2877 | 2.0995 | 2.7 | 13.4 | 14.8 | 24 |  | 2988 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 704 | 767 | 998 |  | 0 | 0 | 0 | 1
36020015 |  |  | 3 | 60 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 2985.6 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 2986 | 3875 | 4083 | 5893 | 257 | 333 | 351 | 507 | 0.40714 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3732 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
36020016 |  |  | 3 | 60 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 2834.24 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2834 | 5667 | 5971 | 8618 | 244 | 487 | 514 | 741 | 1.0105 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 824.6 | 868.3 | 1254 | 0.95 | 0.95 | 0.95 | 825 | 868 | 1254 | 355 | 373 | 539 | 2.0979 | 2.3103 | 4.7413 | 4 | 13.2 | 14.7 | 23.5 |  | 4168 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 825 | 868 | 1254 |  | 0 | 0 | 0 | 1
36020020 |  |  | 3 | 60 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4172.8 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 4173 | 5215 | 5684 | 7393 | 359 | 448 | 489 | 636 | 0.59217 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 5216 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
36020021 |  |  | 3 | 60 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 4611.2 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 4611 | 7299 | 7690 | 11098 | 397 | 628 | 661 | 954 | 1.0713 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 899.3873 | 947.661 | 1367.639 | 0.85 | 0.85 | 0.85 | 899 | 948 | 1368 | 387 | 408 | 588 | 1.0199 | 1.1292 | 2.2871 | 5.3 | 13.2 | 14.7 | 23.5 |  | 5764 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 899 | 948 | 1368 |  | 0 | 0 | 0 | 1
36022010 |  |  | 3 | 60 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2316.6 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2317 | 3561 | 3891 | 5129 | 199 | 306 | 335 | 441 | 0.298 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2574 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
36022011 |  |  | 3 | 60 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2235.16 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2235 | 4831 | 5279 | 6959 | 192 | 415 | 454 | 598 | 0.49962 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 768.7279 | 839.9298 | 1107.263 | 0.95 | 0.95 | 0.95 | 769 | 840 | 1107 | 331 | 361 | 476 | 1.368 | 1.6069 | 2.6863 | 2.9 | 13.4 | 14.8 | 24 |  | 3287 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 769 | 840 | 1107 |  | 0 | 0 | 0 | 1
36022015 |  |  | 3 | 60 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3284 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3284 | 4303 | 4482 | 6541 | 282 | 370 | 385 | 563 | 0.50059 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 4105 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
36022016 |  |  | 3 | 60 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3117.8 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3118 | 6292 | 6554 | 9565 | 268 | 541 | 564 | 823 | 1.238 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 915.1902 | 953.3165 | 1391.275 | 0.95 | 0.95 | 0.95 | 915 | 953 | 1391 | 393 | 410 | 598 | 2.6067 | 2.8308 | 5.9092 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4585 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 915 | 953 | 1391 |  | 0 | 0 | 0 | 1
36022020 |  |  | 3 | 60 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4590.4 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4590 | 5697 | 6224 | 8205 | 395 | 490 | 535 | 706 | 0.72798 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 5738 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
36022021 |  |  | 3 | 60 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5072 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 5072 | 8103 | 8440 | 12318 | 436 | 697 | 726 | 1059 | 1.3186 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 998.5041 | 1040.1012 | 1517.929 | 0.85 | 0.85 | 0.85 | 999 | 1040 | 1518 | 430 | 447 | 653 | 1.2839 | 1.3833 | 2.8718 | 5.9 | 15.5 | 16.8 | 27.5 |  | 6340 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 999 | 1040 | 1518 |  | 0 | 0 | 0 | 1
36024010 |  |  | 3 | 60 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2527.2 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2527 | 3860 | 4229 | 5637 | 217 | 332 | 364 | 485 | 0.36772 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2808 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
36024011 |  |  | 3 | 60 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2438.48 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2438 | 5238 | 5738 | 7648 | 210 | 450 | 493 | 658 | 0.62268 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 833.15 | 912.95 | 1216.95 | 0.95 | 0.95 | 0.95 | 833 | 913 | 1217 | 358 | 393 | 523 | 1.666 | 1.9798 | 3.3626 | 3.2 | 14.8 | 16.6 | 28 |  | 3586 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 833 | 913 | 1217 |  | 0 | 0 | 0 | 1
36024015 |  |  | 3 | 60 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3582.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3582 | 4730 | 4902 | 7188 | 308 | 407 | 422 | 618 | 0.60905 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4478 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
36024016 |  |  | 3 | 60 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3401.36 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3401 | 6916 | 7168 | 10512 | 292 | 595 | 616 | 904 | 1.4916 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1006.05 | 1043.1 | 1529.5 | 0.95 | 0.95 | 0.95 | 1006 | 1043 | 1530 | 433 | 448 | 658 | 3.2057 | 3.4252 | 7.24 | 4.8 | 16.4 | 17.7 | 29.7 |  | 5002 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1006 | 1043 | 1530 |  | 0 | 0 | 0 | 1
36024020 |  |  | 3 | 60 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5007.2 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 5007 | 6176 | 6766 | 9018 | 431 | 531 | 582 | 776 | 0.87958 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 6259 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
36024021 |  |  | 3 | 60 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5533.6 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 5534 | 8907 | 9231 | 13538 | 476 | 766 | 794 | 1164 | 1.6021 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1097.6357 | 1137.5659 | 1668.219 | 0.85 | 0.85 | 0.85 | 1098 | 1138 | 1668 | 472 | 489 | 717 | 1.5763 | 1.6871 | 3.5225 | 6.4 | 16.4 | 17.7 | 29.7 |  | 6917 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1098 | 1138 | 1668 |  | 0 | 0 | 0 | 1
36026010 |  |  | 3 | 60 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2737.8 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2738 | 4178 | 4608 | 6144 | 235 | 359 | 396 | 528 | 0.44656 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 3042 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
36026011 |  |  | 3 | 60 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2641.12 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2641 | 5669 | 6253 | 8337 | 227 | 488 | 538 | 717 | 0.75662 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 902.0356 | 994.8922 | 1326.523 | 0.95 | 0.95 | 0.95 | 902 | 995 | 1327 | 388 | 428 | 571 | 2.0297 | 2.4328 | 4.1463 | 3.5 | 16.2 | 18.6 | 31.4 |  | 3884 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 902 | 995 | 1327 |  | 0 | 0 | 0 | 1
36026015 |  |  | 3 | 60 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3881.6 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 3882 | 4942 | 5122 | 7511 | 334 | 425 | 440 | 646 | 0.72986 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 4852 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
36026016 |  |  | 3 | 60 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3684.24 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3684 | 7342 | 7610 | 11159 | 317 | 631 | 654 | 960 | 1.7828 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1015.4265 | 1052.3662 | 1543.275 | 0.95 | 0.95 | 0.95 | 1015 | 1052 | 1543 | 436 | 452 | 663 | 3.307 | 3.5466 | 7.4671 | 5.2 | 16.4 | 17.7 | 29.7 |  | 5418 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1015 | 1052 | 1543 |  | 0 | 0 | 0 | 1
36026020 |  |  | 3 | 60 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5424.8 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 5425 | 6445 | 7108 | 9477 | 467 | 554 | 611 | 815 | 1.0474 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 6781 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
36026021 |  |  | 3 | 60 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 5994.4 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5994 | 9235 | 9571 | 14035 | 515 | 794 | 823 | 1207 | 1.9104 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1109.137 | 1149.4857 | 1685.699 | 0.85 | 0.85 | 0.85 | 1109 | 1149 | 1686 | 477 | 494 | 725 | 1.6495 | 1.7639 | 3.6829 | 6.9 | 16.4 | 17.7 | 29.7 |  | 7493 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1109 | 1149 | 1686 |  | 0 | 0 | 0 | 1
36028010 |  |  | 3 | 60 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2948.4 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 2948 | 4331 | 4782 | 6370 | 254 | 372 | 411 | 548 | 0.53887 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3276 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
36028011 |  |  | 3 | 60 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2844.44 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 2844 | 5977 | 6599 | 8790 | 245 | 514 | 568 | 756 | 0.91385 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 908.2 | 1003.2 | 1335.7 | 0.95 | 0.95 | 0.95 | 908 | 1003 | 1336 | 390 | 431 | 574 | 2.1462 | 2.5799 | 4.3766 | 3.7 | 16.2 | 18.6 | 31.4 |  | 4183 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 908 | 1003 | 1336 |  | 0 | 0 | 0 | 1
36028015 |  |  | 3 | 60 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4180 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 4180 | 5584 | 5709 | 8484 | 359 | 480 | 491 | 730 | 0.85883 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 5225 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
36028016 |  |  | 3 | 60 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 3967.8 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3968 | 8166 | 8348 | 12406 | 341 | 702 | 718 | 1067 | 2.0914 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1187.5 | 1214.1 | 1805 | 0.95 | 0.95 | 0.95 | 1188 | 1214 | 1805 | 511 | 522 | 776 | 4.5769 | 4.7699 | 10.3006 | 5.6 | 19.3 | 20.4 | 34.5 |  | 5835 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1188 | 1214 | 1805 |  | 0 | 0 | 0 | 1
36028020 |  |  | 3 | 60 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 5841.6 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 5842 | 7237 | 7990 | 10642 | 502 | 622 | 687 | 915 | 1.227 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 7302 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
36028021 |  |  | 3 | 60 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6456 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 6456 | 10516 | 10751 | 15977 | 555 | 904 | 925 | 1374 | 2.2581 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1198.6919 | 1225.5218 | 1821.1391 | 0.85 | 0.85 | 0.85 | 1199 | 1226 | 1821 | 516 | 527 | 783 | 1.9644 | 2.0453 | 4.3663 | 7.5 | 19.3 | 20.4 | 34.5 |  | 8070 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1199 | 1226 | 1821 |  | 0 | 0 | 0 | 1
36030010 |  |  | 3 | 60 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3159 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 3159 | 4485 | 4951 | 6595 | 272 | 386 | 426 | 567 | 0.63762 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 3510 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
36030011 |  |  | 3 | 60 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3047.76 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 3048 | 6285 | 6939 | 9242 | 262 | 541 | 597 | 795 | 1.0822 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 914.85 | 1009.85 | 1345.2 | 0.95 | 0.95 | 0.95 | 915 | 1010 | 1345 | 393 | 434 | 578 | 2.2752 | 2.7301 | 4.6254 | 4 | 16.2 | 18.6 | 31.4 |  | 4482 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 915 | 1010 | 1345 |  | 0 | 0 | 0 | 1
36030015 |  |  | 3 | 60 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4478.4 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 4478 | 5796 | 5926 | 8806 | 385 | 498 | 510 | 757 | 1.0051 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 5598 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
36030016 |  |  | 3 | 60 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4251.36 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 4251 | 8592 | 8784 | 13053 | 366 | 739 | 755 | 1123 | 2.441 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1197 | 1223.6 | 1819.25 | 0.95 | 0.95 | 0.95 | 1197 | 1224 | 1819 | 515 | 526 | 782 | 4.724 | 4.9212 | 10.6148 | 6 | 19.3 | 20.4 | 34.5 |  | 6252 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1197 | 1224 | 1819 |  | 0 | 0 | 0 | 1
36030020 |  |  | 3 | 60 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6259.2 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 6259 | 7549 | 8335 | 11102 | 538 | 649 | 717 | 955 | 1.428 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 7824 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
36030021 |  |  | 3 | 60 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6916.8 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 6917 | 10844 | 11086 | 16475 | 595 | 933 | 953 | 1417 | 2.6397 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1394.6 | 1425.95 | 2119.45 | 0.85 | 0.85 | 0.85 | 1395 | 1426 | 2119 | 600 | 613 | 911 | 2.6822 | 2.7944 | 5.964 | 8 | 19.3 | 20.4 | 34.5 |  | 8646 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1395 | 1426 | 2119 |  | 0 | 0 | 0 | 1
3705010 |  |  | 3 | 70 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 554 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 554 | 649 | 695 | 812 | 48 | 56 | 60 | 70 | 0.010578 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 624 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3705011 |  |  | 3 | 70 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 540.6 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 541 | 881 | 943 | 1102 | 47 | 76 | 81 | 95 | 0.016836 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 132.8052 | 142.1115 | 166.176 | 0.95 | 0.95 | 0.95 | 133 | 142 | 166 | 57 | 61 | 71 | 0.024439 | 0.027864 | 0.037378 | 0.7 | 3.6 | 4.1 | 5.1 |  | 795 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 133 | 142 | 166 |  | 0 | 0 | 0 | 1
3706010 |  |  | 3 | 70 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 674.1 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 674 | 842 | 901 | 1066 | 58 | 72 | 77 | 92 | 0.016172 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 749 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3706011 |  |  | 3 | 70 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 648.72 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 649 | 1142 | 1223 | 1447 | 56 | 98 | 105 | 124 | 0.025294 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 171.9 | 184.5 | 217.8 | 0.95 | 0.95 | 0.95 | 172 | 185 | 218 | 74 | 80 | 94 | 0.043216 | 0.050211 | 0.068502 | 0.8 | 4.8 | 5.4 | 6.8 |  | 954 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 172 | 185 | 218 |  | 0 | 0 | 0 | 1
3706015 |  |  | 3 | 70 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1183 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3706016 |  |  | 3 | 70 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 922.08 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 922 | 1400 | 1503 | 1989 | 79 | 120 | 129 | 171 | 0.092143 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 192.6 | 207 | 274.5 | 0.95 | 0.95 | 0.95 | 193 | 207 | 275 | 83 | 89 | 118 | 0.10161 | 0.11666 | 0.20395 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1356 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 193 | 207 | 275 |  | 0 | 0 | 0 | 1
3706020 |  |  | 3 | 70 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1652 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3706021 |  |  | 3 | 70 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1524.8 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1525 | 1803 | 1935 | 2561 | 131 | 155 | 166 | 220 | 0.096566 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 210.4464 | 225.9095 | 298.998 | 0.85 | 0.85 | 0.85 | 210 | 226 | 299 | 90 | 97 | 129 | 0.046103 | 0.053427 | 0.093682 | 1.6 | 4.8 | 5.5 | 7.2 |  | 1906 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 210 | 226 | 299 |  | 0 | 0 | 0 | 1
3707010 |  |  | 3 | 70 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 786.6 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 787 | 1030 | 1104 | 1320 | 68 | 89 | 95 | 114 | 0.023173 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 874 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3707011 |  |  | 3 | 70 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 756.84 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 757 | 1397 | 1498 | 1791 | 65 | 120 | 129 | 154 | 0.035849 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 210.6121 | 225.8589 | 270.036 | 0.95 | 0.95 | 0.95 | 211 | 226 | 270 | 91 | 97 | 116 | 0.068243 | 0.077125 | 0.1087 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1113 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 211 | 226 | 270 |  | 0 | 0 | 0 | 1
3707015 |  |  | 3 | 70 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1380 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3707016 |  |  | 3 | 70 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1075.76 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1076 | 1628 | 1747 | 2313 | 93 | 140 | 150 | 199 | 0.12929 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 197.6379 | 212.1599 | 280.8 | 0.95 | 0.95 | 0.95 | 198 | 212 | 281 | 85 | 91 | 121 | 0.10824 | 0.12386 | 0.21753 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1582 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 198 | 212 | 281 |  | 0 | 0 | 0 | 1
3707020 |  |  | 3 | 70 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 1927 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3707021 |  |  | 3 | 70 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1779.2 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1779 | 1978 | 2123 | 2810 | 153 | 170 | 183 | 242 | 0.13403 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 216.2742 | 232.1655 | 307.278 | 0.85 | 0.85 | 0.85 | 216 | 232 | 307 | 93 | 100 | 132 | 0.050403 | 0.058119 | 0.10027 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2224 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 216 | 232 | 307 |  | 0 | 0 | 0 | 1
3708010 |  |  | 3 | 70 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 898.2 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 898 | 1214 | 1304 | 1574 | 77 | 104 | 112 | 135 | 0.030898 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 998 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3708011 |  |  | 3 | 70 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 864.96 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 865 | 1648 | 1770 | 2136 | 74 | 142 | 152 | 184 | 0.048653 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 248.4 | 266.4 | 322.2 | 0.95 | 0.95 | 0.95 | 248 | 266 | 322 | 107 | 114 | 138 | 0.098245 | 0.11088 | 0.15975 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1272 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 248 | 266 | 322 |  | 0 | 0 | 0 | 1
3708015 |  |  | 3 | 70 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1262.4 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1262 | 1395 | 1496 | 2008 | 109 | 120 | 129 | 173 | 0.06249 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1578 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3708016 |  |  | 3 | 70 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1229.44 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1229 | 2040 | 2188 | 2936 | 106 | 175 | 188 | 252 | 0.16998 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 280.8 | 301.5 | 405 | 0.95 | 0.95 | 0.95 | 281 | 302 | 405 | 121 | 130 | 174 | 0.22071 | 0.2543 | 0.4523 | 1.6 | 6 | 6.7 | 9 |  | 1808 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 281 | 302 | 405 |  | 0 | 0 | 0 | 1
3708020 |  |  | 3 | 70 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1761.6 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1762 | 1943 | 2086 | 2518 | 152 | 167 | 179 | 217 | 0.094646 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2202 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3708021 |  |  | 3 | 70 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2033.6 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 2034 | 2628 | 2818 | 3781 | 175 | 226 | 242 | 325 | 0.17822 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 306.776 | 328.9638 | 441.378 | 0.85 | 0.85 | 0.85 | 307 | 329 | 441 | 132 | 141 | 190 | 0.10251 | 0.11666 | 0.20945 | 2.1 | 6 | 6.7 | 9 |  | 2542 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 307 | 329 | 441 |  | 0 | 0 | 0 | 1
3709010 |  |  | 3 | 70 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1010.7 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 1011 | 1396 | 1501 | 1828 | 87 | 120 | 129 | 157 | 0.040855 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1123 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3709011 |  |  | 3 | 70 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 973.08 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 973 | 1894 | 2037 | 2480 | 84 | 163 | 175 | 213 | 0.065317 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 285.4467 | 307.0599 | 373.896 | 0.95 | 0.95 | 0.95 | 285 | 307 | 374 | 123 | 132 | 161 | 0.13476 | 0.15415 | 0.22503 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1431 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 285 | 307 | 374 |  | 0 | 0 | 0 | 1
3709015 |  |  | 3 | 70 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1420 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1420 | 1598 | 1712 | 2331 | 122 | 137 | 147 | 200 | 0.079564 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1775 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3709016 |  |  | 3 | 70 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1383.12 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1383 | 2337 | 2503 | 3409 | 119 | 201 | 215 | 293 | 0.21666 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322.0014 | 344.9732 | 469.8 | 0.95 | 0.95 | 0.95 | 322 | 345 | 470 | 138 | 148 | 202 | 0.29011 | 0.33302 | 0.61515 | 1.8 | 7 | 7.7 | 10.7 |  | 2034 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 322 | 345 | 470 |  | 0 | 0 | 0 | 1
3709020 |  |  | 3 | 70 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 1982.4 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 1982 | 2233 | 2402 | 2925 | 170 | 192 | 207 | 252 | 0.11976 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2478 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3709021 |  |  | 3 | 70 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2287.2 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2287 | 3009 | 3224 | 4391 | 197 | 259 | 277 | 378 | 0.22933 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 351.3147 | 376.3777 | 512.568 | 0.85 | 0.85 | 0.85 | 351 | 376 | 513 | 151 | 162 | 221 | 0.13626 | 0.15636 | 0.28728 | 2.4 | 7 | 7.7 | 10.7 |  | 2859 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 351 | 376 | 513 |  | 0 | 0 | 0 | 1
37010010 |  |  | 3 | 70 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1123.2 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1123 | 1574 | 1696 | 2082 | 97 | 135 | 146 | 179 | 0.052479 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1248 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
37010011 |  |  | 3 | 70 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1081.2 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1081 | 2136 | 2301 | 2825 | 93 | 184 | 198 | 243 | 0.083268 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 322.2 | 346.5 | 425.7 | 0.95 | 0.95 | 0.95 | 322 | 347 | 426 | 138 | 149 | 183 | 0.17577 | 0.2033 | 0.30039 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1590 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 322 | 347 | 426 |  | 0 | 0 | 0 | 1
37010015 |  |  | 3 | 70 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1577.6 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1578 | 1799 | 1926 | 2655 | 136 | 155 | 166 | 228 | 0.10037 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 1972 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
37010016 |  |  | 3 | 70 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1536.8 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1537 | 2630 | 2817 | 3883 | 132 | 226 | 242 | 334 | 0.26947 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 362.7 | 387.9 | 535.5 | 0.95 | 0.95 | 0.95 | 363 | 388 | 536 | 156 | 167 | 230 | 0.37438 | 0.42814 | 0.80448 | 2 | 7 | 7.7 | 10.7 |  | 2260 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 363 | 388 | 536 |  | 0 | 0 | 0 | 1
37010020 |  |  | 3 | 70 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2202.4 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2202 | 2519 | 2714 | 3331 | 189 | 217 | 233 | 286 | 0.14964 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2753 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
37010021 |  |  | 3 | 70 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2541.6 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 2542 | 3388 | 3627 | 5000 | 219 | 291 | 312 | 430 | 0.28756 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 395.4747 | 423.466 | 583.758 | 0.85 | 0.85 | 0.85 | 395 | 423 | 584 | 170 | 182 | 251 | 0.1753 | 0.20028 | 0.3755 | 2.7 | 7 | 7.7 | 10.7 |  | 3177 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 395 | 423 | 584 |  | 0 | 0 | 0 | 1
37011010 |  |  | 3 | 70 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1235.7 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1236 | 1766 | 1903 | 2336 | 106 | 152 | 164 | 201 | 0.064687 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1373 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
37011011 |  |  | 3 | 70 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1189.32 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1189 | 2397 | 2582 | 3169 | 102 | 206 | 222 | 273 | 0.1039 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 361.2785 | 389.2135 | 477.756 | 0.95 | 0.95 | 0.95 | 361 | 389 | 478 | 155 | 167 | 206 | 0.22892 | 0.26361 | 0.39231 | 1.5 | 8.4 | 9.3 | 14 |  | 1749 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 361 | 389 | 478 |  | 0 | 0 | 0 | 1
37011015 |  |  | 3 | 70 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1735.2 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1735 | 1908 | 2043 | 2817 | 149 | 164 | 176 | 242 | 0.12226 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2169 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
37011016 |  |  | 3 | 70 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1690.48 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1690 | 2850 | 3051 | 4207 | 145 | 245 | 262 | 362 | 0.32853 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 367.0497 | 393.0291 | 541.8 | 0.95 | 0.95 | 0.95 | 367 | 393 | 542 | 158 | 169 | 233 | 0.38893 | 0.44395 | 0.83515 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2486 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 367 | 393 | 542 |  | 0 | 0 | 0 | 1
37011020 |  |  | 3 | 70 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2422.4 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2422 | 2693 | 2901 | 3561 | 208 | 232 | 249 | 306 | 0.18312 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 3028 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
37011021 |  |  | 3 | 70 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 2796 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 2796 | 3556 | 3808 | 5249 | 240 | 306 | 327 | 451 | 0.35025 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 401.0841 | 429.4724 | 592.038 | 0.85 | 0.85 | 0.85 | 401 | 429 | 592 | 172 | 184 | 255 | 0.18288 | 0.20857 | 0.39426 | 2.9 | 7.9 | 8.8 | 12.5 |  | 3495 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 401 | 429 | 592 |  | 0 | 0 | 0 | 1
37012010 |  |  | 3 | 70 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1348.2 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1348 | 1925 | 2080 | 2590 | 116 | 166 | 179 | 223 | 0.079746 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1498 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
37012011 |  |  | 3 | 70 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1297.44 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1297 | 2612 | 2822 | 3514 | 112 | 225 | 243 | 302 | 0.12951 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 393.3 | 425.7 | 530.1 | 0.95 | 0.95 | 0.95 | 393 | 426 | 530 | 169 | 183 | 228 | 0.281 | 0.32654 | 0.49473 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1908 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 393 | 426 | 530 |  | 0 | 0 | 0 | 1
37012015 |  |  | 3 | 70 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 1892.8 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 1893 | 2217 | 2374 | 3303 | 163 | 191 | 204 | 284 | 0.14833 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2366 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
37012016 |  |  | 3 | 70 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 1844.16 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1844 | 3242 | 3472 | 4830 | 159 | 279 | 299 | 415 | 0.39888 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 446.4 | 478.8 | 666 | 0.95 | 0.95 | 0.95 | 446 | 479 | 666 | 192 | 206 | 286 | 0.57765 | 0.66332 | 1.2645 | 2.4 | 8.7 | 9.8 | 14.3 |  | 2712 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 446 | 479 | 666 |  | 0 | 0 | 0 | 1
37012020 |  |  | 3 | 70 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2643.2 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2643 | 3080 | 3327 | 4143 | 227 | 265 | 286 | 356 | 0.22029 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3304 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
37012021 |  |  | 3 | 70 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3049.6 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3050 | 4175 | 4471 | 6220 | 262 | 359 | 385 | 535 | 0.42298 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 487.4047 | 521.9416 | 726.138 | 0.85 | 0.85 | 0.85 | 487 | 522 | 726 | 209 | 224 | 312 | 0.27234 | 0.31169 | 0.59464 | 3.2 | 8.7 | 9.8 | 14.3 |  | 3812 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 487 | 522 | 726 |  | 0 | 0 | 0 | 1
37014010 |  |  | 3 | 70 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1572.3 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1572 | 2268 | 2456 | 3098 | 135 | 195 | 211 | 266 | 0.11405 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1747 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
37014011 |  |  | 3 | 70 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1513.68 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1514 | 3077 | 3333 | 4203 | 130 | 265 | 287 | 361 | 0.18585 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 463.5 | 502.2 | 633.6 | 0.95 | 0.95 | 0.95 | 464 | 502 | 634 | 200 | 216 | 273 | 0.41669 | 0.48151 | 0.74809 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2226 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 464 | 502 | 634 |  | 0 | 0 | 0 | 1
37014015 |  |  | 3 | 70 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2208.8 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2209 | 2629 | 2815 | 3950 | 190 | 226 | 242 | 340 | 0.20689 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2761 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
37014016 |  |  | 3 | 70 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2151.52 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2152 | 3844 | 4117 | 5777 | 185 | 331 | 354 | 497 | 0.55024 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 530.1 | 567 | 796.5 | 0.95 | 0.95 | 0.95 | 530 | 567 | 797 | 228 | 244 | 343 | 0.82869 | 0.94654 | 1.8467 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3164 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 530 | 567 | 797 |  | 0 | 0 | 0 | 1
37014020 |  |  | 3 | 70 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3083.2 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3083 | 3628 | 3929 | 4956 | 265 | 312 | 338 | 426 | 0.30593 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 3854 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
37014021 |  |  | 3 | 70 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 3558.4 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 3558 | 4951 | 5302 | 7440 | 306 | 426 | 456 | 640 | 0.5916 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 578.0031 | 619.0009 | 868.518 | 0.85 | 0.85 | 0.85 | 578 | 619 | 869 | 249 | 266 | 374 | 0.39641 | 0.45064 | 0.87404 | 3.7 | 9.6 | 10.5 | 16.1 |  | 4448 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 578 | 619 | 869 |  | 0 | 0 | 0 | 1
37016010 |  |  | 3 | 70 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1797.3 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1797 | 2604 | 2827 | 3605 | 155 | 224 | 243 | 310 | 0.15785 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 1997 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
37016011 |  |  | 3 | 70 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1729.92 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1730 | 3533 | 3835 | 4892 | 149 | 304 | 330 | 421 | 0.25822 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 532.8 | 577.8 | 737.1 | 0.95 | 0.95 | 0.95 | 533 | 578 | 737 | 229 | 249 | 317 | 0.57601 | 0.67371 | 1.0593 | 2.1 | 11 | 12.4 | 19.2 |  | 2544 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 533 | 578 | 737 |  | 0 | 0 | 0 | 1
37016015 |  |  | 3 | 70 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2524 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2524 | 3021 | 3226 | 4598 | 217 | 260 | 277 | 395 | 0.27653 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 3155 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
37016016 |  |  | 3 | 70 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2458.88 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2459 | 4418 | 4717 | 6724 | 211 | 380 | 406 | 578 | 0.72852 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 608.4 | 649.8 | 927 | 0.95 | 0.95 | 0.95 | 608 | 650 | 927 | 261 | 280 | 399 | 1.1042 | 1.2669 | 2.5354 | 3.2 | 11.5 | 12.8 | 19.6 |  | 3616 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 608 | 650 | 927 |  | 0 | 0 | 0 | 1
37016020 |  |  | 3 | 70 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3524 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3524 | 4166 | 4522 | 5768 | 303 | 358 | 389 | 496 | 0.40709 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 4405 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
37016021 |  |  | 3 | 70 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4066.4 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 4066 | 5690 | 6075 | 8659 | 350 | 489 | 522 | 745 | 0.79225 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 664.23 | 709.1764 | 1010.898 | 0.85 | 0.85 | 0.85 | 664 | 709 | 1011 | 286 | 305 | 435 | 0.53575 | 0.60681 | 1.2079 | 4.3 | 11.5 | 12.8 | 19.6 |  | 5083 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 664 | 709 | 1011 |  | 0 | 0 | 0 | 1
37018010 |  |  | 3 | 70 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2021.4 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 2021 | 2971 | 3225 | 4113 | 174 | 256 | 277 | 354 | 0.20818 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 2246 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
37018011 |  |  | 3 | 70 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 1946.16 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1946 | 4031 | 4376 | 5581 | 167 | 347 | 376 | 480 | 0.3417 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 607.5928 | 659.5714 | 841.266 | 0.95 | 0.95 | 0.95 | 608 | 660 | 841 | 261 | 284 | 362 | 0.78419 | 0.91797 | 1.4444 | 2.4 | 12.2 | 13.7 | 22 |  | 2862 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 608 | 660 | 841 |  | 0 | 0 | 0 | 1
37018015 |  |  | 3 | 70 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2840 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 2840 | 3233 | 3452 | 4921 | 244 | 278 | 297 | 423 | 0.35774 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3550 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
37018016 |  |  | 3 | 70 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2766.24 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 2766 | 4843 | 5171 | 7371 | 238 | 417 | 445 | 634 | 0.9423 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 617.678 | 659.4743 | 940.05 | 0.95 | 0.95 | 0.95 | 618 | 659 | 940 | 266 | 283 | 404 | 1.1707 | 1.3212 | 2.649 | 3.6 | 11.5 | 12.8 | 19.6 |  | 4068 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 618 | 659 | 940 |  | 0 | 0 | 0 | 1
37018020 |  |  | 3 | 70 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3964 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3964 | 4498 | 4883 | 6228 | 341 | 387 | 420 | 536 | 0.5243 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 4955 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
37018021 |  |  | 3 | 70 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4575.2 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 4575 | 6017 | 6424 | 9157 | 393 | 517 | 552 | 788 | 1.0212 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 675.1111 | 720.7938 | 1027.458 | 0.85 | 0.85 | 0.85 | 675 | 721 | 1027 | 290 | 310 | 442 | 0.56774 | 0.64573 | 1.2819 | 4.8 | 11.5 | 12.8 | 19.6 |  | 5719 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 675 | 721 | 1027 |  | 0 | 0 | 0 | 1
37020010 |  |  | 3 | 70 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2246.4 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 2246 | 3260 | 3553 | 4621 | 193 | 280 | 306 | 397 | 0.26715 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2496 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
37020011 |  |  | 3 | 70 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2162.4 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2162 | 4423 | 4821 | 6270 | 186 | 380 | 415 | 539 | 0.44431 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 666.9 | 726.3 | 945 | 0.95 | 0.95 | 0.95 | 667 | 726 | 945 | 287 | 312 | 406 | 0.99322 | 1.1601 | 1.8944 | 2.7 | 13.4 | 14.8 | 24 |  | 3180 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 667 | 726 | 945 |  | 0 | 0 | 0 | 1
37020015 |  |  | 3 | 70 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3155.2 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 3155 | 3875 | 4083 | 5893 | 271 | 333 | 351 | 507 | 0.45096 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 3944 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
37020016 |  |  | 3 | 70 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3073.6 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3074 | 5667 | 5971 | 8618 | 264 | 487 | 514 | 741 | 1.178 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 781.2 | 822.6 | 1188 | 0.95 | 0.95 | 0.95 | 781 | 823 | 1188 | 336 | 354 | 511 | 1.8845 | 2.0864 | 4.2719 | 4 | 13.2 | 14.7 | 23.5 |  | 4520 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 781 | 823 | 1188 |  | 0 | 0 | 0 | 1
37020020 |  |  | 3 | 70 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4404.8 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 4405 | 5215 | 5684 | 7393 | 379 | 448 | 489 | 636 | 0.65804 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 5506 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
37020021 |  |  | 3 | 70 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 5083.2 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 5083 | 7299 | 7690 | 11098 | 437 | 628 | 661 | 954 | 1.2892 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 852.0512 | 897.7841 | 1295.658 | 0.85 | 0.85 | 0.85 | 852 | 898 | 1296 | 366 | 386 | 557 | 0.91589 | 1.0148 | 2.0598 | 5.3 | 13.2 | 14.7 | 23.5 |  | 6354 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 852 | 898 | 1296 |  | 0 | 0 | 0 | 1
37022010 |  |  | 3 | 70 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2471.4 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2471 | 3561 | 3891 | 5129 | 213 | 306 | 335 | 441 | 0.33822 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 2746 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
37022011 |  |  | 3 | 70 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2378.64 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2379 | 4831 | 5279 | 6959 | 205 | 415 | 454 | 598 | 0.56383 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 728.2686 | 795.7229 | 1048.986 | 0.95 | 0.95 | 0.95 | 728 | 796 | 1049 | 313 | 342 | 451 | 1.2333 | 1.4535 | 2.4298 | 2.9 | 13.4 | 14.8 | 24 |  | 3498 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 728 | 796 | 1049 |  | 0 | 0 | 0 | 1
37022015 |  |  | 3 | 70 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3470.4 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3470 | 4303 | 4482 | 6541 | 298 | 370 | 385 | 563 | 0.55663 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 4338 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
37022016 |  |  | 3 | 70 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3380.96 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3381 | 6292 | 6554 | 9565 | 291 | 541 | 564 | 823 | 1.4528 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 867.0223 | 903.142 | 1318.05 | 0.95 | 0.95 | 0.95 | 867 | 903 | 1318 | 373 | 388 | 567 | 2.3547 | 2.5425 | 5.3261 | 4.4 | 15.5 | 16.8 | 27.5 |  | 4972 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 867 | 903 | 1318 |  | 0 | 0 | 0 | 1
37022020 |  |  | 3 | 70 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 4845.6 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 4846 | 5697 | 6224 | 8205 | 417 | 490 | 535 | 706 | 0.8088 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 6057 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
37022021 |  |  | 3 | 70 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 5591.2 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 5591 | 8103 | 8440 | 12318 | 481 | 697 | 726 | 1059 | 1.593 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 945.9512 | 985.3591 | 1438.038 | 0.85 | 0.85 | 0.85 | 946 | 985 | 1438 | 407 | 424 | 618 | 1.1551 | 1.2497 | 2.5822 | 5.9 | 15.5 | 16.8 | 27.5 |  | 6989 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 946 | 985 | 1438 |  | 0 | 0 | 0 | 1
37024010 |  |  | 3 | 70 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2695.5 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2696 | 3860 | 4229 | 5637 | 232 | 332 | 364 | 485 | 0.41633 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 2995 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
37024011 |  |  | 3 | 70 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2594.88 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2595 | 5238 | 5738 | 7648 | 223 | 450 | 493 | 658 | 0.69548 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 789.3 | 864.9 | 1152.9 | 0.95 | 0.95 | 0.95 | 789 | 865 | 1153 | 339 | 372 | 496 | 1.5062 | 1.7885 | 3.0476 | 3.2 | 14.8 | 16.6 | 28 |  | 3816 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 789 | 865 | 1153 |  | 0 | 0 | 0 | 1
37024015 |  |  | 3 | 70 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 3786.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 3786 | 4730 | 4902 | 7188 | 326 | 407 | 422 | 618 | 0.67918 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 4733 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
37024016 |  |  | 3 | 70 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3688.32 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3688 | 6916 | 7168 | 10512 | 317 | 595 | 616 | 904 | 1.7493 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 953.1 | 988.2 | 1449 | 0.95 | 0.95 | 0.95 | 953 | 988 | 1449 | 410 | 425 | 623 | 2.883 | 3.0915 | 6.5084 | 4.8 | 16.4 | 17.7 | 29.7 |  | 5424 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 953 | 988 | 1449 |  | 0 | 0 | 0 | 1
37024020 |  |  | 3 | 70 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5285.6 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 5286 | 6176 | 6766 | 9018 | 455 | 531 | 582 | 776 | 0.97703 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 6607 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
37024021 |  |  | 3 | 70 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6100 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 6100 | 8907 | 9231 | 13538 | 525 | 766 | 794 | 1164 | 1.9338 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1039.8654 | 1077.694 | 1580.418 | 0.85 | 0.85 | 0.85 | 1040 | 1078 | 1580 | 447 | 464 | 679 | 1.42 | 1.5254 | 3.1718 | 6.4 | 16.4 | 17.7 | 29.7 |  | 7625 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1040 | 1078 | 1580 |  | 0 | 0 | 0 | 1
37026010 |  |  | 3 | 70 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 2920.5 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 2921 | 4178 | 4608 | 6144 | 251 | 359 | 396 | 528 | 0.50454 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 3245 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
37026011 |  |  | 3 | 70 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 2811.12 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2811 | 5669 | 6253 | 8337 | 242 | 488 | 538 | 717 | 0.85099 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 854.5601 | 942.5295 | 1256.706 | 0.95 | 0.95 | 0.95 | 855 | 943 | 1257 | 368 | 405 | 541 | 1.8409 | 2.1969 | 3.752 | 3.5 | 16.2 | 18.6 | 31.4 |  | 4134 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 855 | 943 | 1257 |  | 0 | 0 | 0 | 1
37026015 |  |  | 3 | 70 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4101.6 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 4102 | 4942 | 5122 | 7511 | 353 | 425 | 440 | 646 | 0.81145 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 5127 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
37026016 |  |  | 3 | 70 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 3995.68 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3996 | 7342 | 7610 | 11159 | 344 | 631 | 654 | 960 | 2.0886 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 961.983 | 996.9785 | 1462.05 | 0.95 | 0.95 | 0.95 | 962 | 997 | 1462 | 414 | 429 | 629 | 2.9909 | 3.2048 | 6.7402 | 5.2 | 16.4 | 17.7 | 29.7 |  | 5876 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 962 | 997 | 1462 |  | 0 | 0 | 0 | 1
37026020 |  |  | 3 | 70 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5726.4 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 5726 | 6445 | 7108 | 9477 | 492 | 554 | 611 | 815 | 1.1586 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 7158 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
37026021 |  |  | 3 | 70 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 6608 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 6608 | 9235 | 9571 | 14035 | 568 | 794 | 823 | 1207 | 2.3051 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1050.7614 | 1088.9865 | 1596.978 | 0.85 | 0.85 | 0.85 | 1051 | 1089 | 1597 | 452 | 468 | 687 | 1.4879 | 1.5904 | 3.3209 | 6.9 | 16.4 | 17.7 | 29.7 |  | 8260 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 1051 | 1089 | 1597 |  | 0 | 0 | 0 | 1
37028010 |  |  | 3 | 70 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3144.6 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 3145 | 4331 | 4782 | 6370 | 270 | 372 | 411 | 548 | 0.60333 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3494 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
37028011 |  |  | 3 | 70 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3027.36 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 3027 | 5977 | 6599 | 8790 | 260 | 514 | 568 | 756 | 1.019 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 860.4 | 950.4 | 1265.4 | 0.95 | 0.95 | 0.95 | 860 | 950 | 1265 | 370 | 409 | 544 | 1.9481 | 2.3426 | 3.9636 | 3.7 | 16.2 | 18.6 | 31.4 |  | 4452 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 860 | 950 | 1265 |  | 0 | 0 | 0 | 1
37028015 |  |  | 3 | 70 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4417.6 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 4418 | 5584 | 5709 | 8484 | 380 | 480 | 491 | 730 | 0.95744 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 5522 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
37028016 |  |  | 3 | 70 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4303.04 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 4303 | 8166 | 8348 | 12406 | 370 | 702 | 718 | 1067 | 2.4491 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1125 | 1150.2 | 1710 | 0.95 | 0.95 | 0.95 | 1125 | 1150 | 1710 | 484 | 495 | 735 | 4.1198 | 4.3032 | 9.2691 | 5.6 | 19.3 | 20.4 | 34.5 |  | 6328 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1125 | 1150 | 1710 |  | 0 | 0 | 0 | 1
37028020 |  |  | 3 | 70 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6166.4 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 6166 | 7237 | 7990 | 10642 | 530 | 622 | 687 | 915 | 1.3628 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 7708 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
37028021 |  |  | 3 | 70 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7116.8 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 7117 | 10516 | 10751 | 15977 | 612 | 904 | 925 | 1374 | 2.7227 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1135.6028 | 1161.0206 | 1725.2896 | 0.85 | 0.85 | 0.85 | 1136 | 1161 | 1725 | 488 | 499 | 742 | 1.7657 | 1.8426 | 3.9383 | 7.5 | 19.3 | 20.4 | 34.5 |  | 8896 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1136 | 1161 | 1725 |  | 0 | 0 | 0 | 1
37030010 |  |  | 3 | 70 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3369.6 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 3370 | 4485 | 4951 | 6595 | 290 | 386 | 426 | 567 | 0.71769 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 3744 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
37030011 |  |  | 3 | 70 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3243.6 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 3244 | 6285 | 6939 | 9242 | 279 | 541 | 597 | 795 | 1.2141 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 866.7 | 956.7 | 1274.4 | 0.95 | 0.95 | 0.95 | 867 | 957 | 1274 | 373 | 412 | 548 | 2.0672 | 2.4812 | 4.1928 | 4 | 16.2 | 18.6 | 31.4 |  | 4770 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 867 | 957 | 1274 |  | 0 | 0 | 0 | 1
37030015 |  |  | 3 | 70 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4732.8 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 4733 | 5796 | 5926 | 8806 | 407 | 498 | 510 | 757 | 1.1175 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 5916 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
37030016 |  |  | 3 | 70 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4610.4 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 4610 | 8592 | 8784 | 13053 | 396 | 739 | 755 | 1123 | 2.8422 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1134 | 1159.2 | 1723.5 | 0.95 | 0.95 | 0.95 | 1134 | 1159 | 1724 | 488 | 498 | 741 | 4.2565 | 4.4268 | 9.5614 | 6 | 19.3 | 20.4 | 34.5 |  | 6780 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1134 | 1159 | 1724 |  | 0 | 0 | 0 | 1
37030020 |  |  | 3 | 70 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6607.2 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 6607 | 7549 | 8335 | 11102 | 568 | 649 | 717 | 955 | 1.5857 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 8259 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
37030021 |  |  | 3 | 70 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7624.8 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 7625 | 10844 | 11086 | 16475 | 656 | 933 | 953 | 1417 | 3.1809 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1321.2 | 1350.9 | 2007.9 | 0.85 | 0.85 | 0.85 | 1321 | 1351 | 2008 | 568 | 581 | 863 | 2.4157 | 2.5224 | 5.3764 | 8 | 19.3 | 20.4 | 34.5 |  | 9531 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1321 | 1351 | 2008 |  | 0 | 0 | 0 | 1
3905010 |  |  | 3 | 90 | 50 | 10 | 11.5 | 0 | 26 | 30 | 38.8 | 554 | 649 | 695 | 812 | 1.5 | 1.08 | 1.08 | 1.08 | 554 | 649 | 695 | 812 | 48 | 56 | 60 | 70 | 0.010578 | 0.014274 | 0.016323 | 0.022034 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 90.0201 | 96.3283 | 112.64 | 0.98 | 0.98 | 0.98 | 90 | 96 | 113 | 39 | 41 | 49 | 0.0070687 | 0.0077891 | 0.011011 | 0.3 | 3.6 | 4.1 | 5.1 |  | 685 |  | 90% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 90 | 96 | 113 |  | 0 | 0 | 0 | 1
3905011 |  |  | 3 | 90 | 50 | 11 | 11.5 | 0 | 26 | 30 | 38.8 | 597.72 | 881.0208 | 942.7581 | 1102.4 | 1.5 | 1.1 | 1.1 | 1.1 | 598 | 881 | 943 | 1102 | 51 | 76 | 81 | 95 | 0.019713 | 0.042644 | 0.048246 | 0.06572 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 118.0491 | 126.3214 | 147.712 | 0.95 | 0.95 | 0.95 | 118 | 126 | 148 | 51 | 54 | 64 | 0.019713 | 0.022014 | 0.030576 | 0.7 | 3.6 | 4.1 | 5.1 |  | 879 |  | 68% |  |  | 0 | 14.2 | 16.2 | 21.85 |  | 1 | 1 | 1 | 118 | 126 | 148 |  | 0 | 0 | 0 | 1
3906010 |  |  | 3 | 90 | 60 | 10 | 11.5 | 0 | 26 | 30 | 40 | 738.9 | 841.6923 | 901.3595 | 1066.38 | 1.5 | 1.08 | 1.08 | 1.08 | 739 | 842 | 901 | 1066 | 64 | 72 | 77 | 92 | 0.019564 | 0.024573 | 0.027985 | 0.039513 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 116.6899 | 124.962 | 147.84 | 0.98 | 0.98 | 0.98 | 117 | 125 | 148 | 50 | 54 | 64 | 0.01214 | 0.014086 | 0.019564 | 0.4 | 4.8 | 5.4 | 6.8 |  | 821 |  | 90% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 117 | 125 | 148 |  | 0 | 0 | 0 | 1
3906011 |  |  | 3 | 90 | 60 | 11 | 11.5 | 0 | 26 | 30 | 40 | 717.4 | 1142.0362 | 1222.9947 | 1446.9 | 1.5 | 1.1 | 1.1 | 1.1 | 717 | 1142 | 1223 | 1447 | 62 | 98 | 105 | 124 | 0.030755 | 0.074231 | 0.084794 | 0.11689 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 152.8 | 164 | 193.6 | 0.95 | 0.95 | 0.95 | 153 | 164 | 194 | 66 | 71 | 83 | 0.034681 | 0.039909 | 0.053899 | 0.8 | 4.8 | 5.4 | 6.8 |  | 1055 |  | 68% |  |  | 0 | 13.6 | 15.6 | 21.85 |  | 1 | 1 | 1 | 153 | 164 | 194 |  | 0 | 0 | 0 | 1
3906015 |  |  | 3 | 90 | 60 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 862.1926 | 957.1926 | 1027.5251 | 1359.96 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 957 | 1028 | 1360 | 74 | 82 | 88 | 117 | 0.027892 | 0.034142 | 0.039239 | 0.068802 | 0.0002083 | 1.724 | 2 | 0.00046183 | 130.6606 | 140.2613 | 185.64 | 1.01 | 1.01 | 1.01 | 131 | 140 | 186 | 56 | 60 | 80 | 0.016115 | 0.018458 | 0.032521 | 0.6 | 4.8 | 5.5 | 7.2 |  | 1272 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 131 | 140 | 186 |  | 0 | 0 | 0 | 1
3906016 |  |  | 3 | 90 | 60 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1059.44 | 1399.7242 | 1502.5729 | 1988.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1059 | 1400 | 1503 | 1989 | 91 | 120 | 129 | 171 | 0.12191 | 0.21086 | 0.24334 | 0.42546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 171.2 | 184 | 244 | 0.95 | 0.95 | 0.95 | 171 | 184 | 244 | 74 | 79 | 105 | 0.08096 | 0.092143 | 0.16185 | 1.2 | 4.8 | 5.5 | 7.2 |  | 1558 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 184 | 244 |  | 0 | 0 | 0 | 1
3906020 |  |  | 3 | 90 | 60 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1251.575 | 1346.575 | 1442.0332 | 1706.04 | 1.5 | 1.08 | 1.08 | 1.08 | 1252 | 1347 | 1442 | 1706 | 108 | 116 | 124 | 147 | 0.046667 | 0.053755 | 0.061339 | 0.085906 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 166.4157 | 178.2129 | 210.84 | 0.95 | 0.95 | 0.95 | 166 | 178 | 211 | 71 | 77 | 91 | 0.020362 | 0.023903 | 0.033257 | 0.8 | 4.8 | 5.5 | 7.2 |  | 1774 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 166 | 178 | 211 |  | 0 | 0 | 0 | 1
3906021 |  |  | 3 | 90 | 60 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1707.6437 | 1802.6437 | 1935.0981 | 2561.16 | 1.5 | 1.05 | 1.05 | 1.05 | 1708 | 1803 | 1935 | 2561 | 147 | 155 | 166 | 220 | 0.12119 | 0.13454 | 0.15403 | 0.26853 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 187.0635 | 200.8085 | 265.776 | 0.85 | 0.85 | 0.85 | 187 | 201 | 266 | 80 | 86 | 114 | 0.036566 | 0.042158 | 0.07343 | 1.6 | 4.8 | 5.5 | 7.2 |  | 2262 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 266 |  | 0 | 0 | 0 | 1
3907010 |  |  | 3 | 90 | 70 | 10 | 11.5 | 0 | 26 | 30 | 41 | 862.2 | 1029.7404 | 1104.286 | 1320.28 | 1.5 | 1.08 | 1.08 | 1.08 | 862 | 1030 | 1104 | 1320 | 74 | 89 | 95 | 114 | 0.027271 | 0.038925 | 0.044147 | 0.062778 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 142.7604 | 153.0952 | 183.04 | 0.98 | 0.98 | 0.98 | 143 | 153 | 183 | 61 | 66 | 79 | 0.018801 | 0.021879 | 0.030933 | 0.5 | 5.5 | 5.9 | 7.9 |  | 958 |  | 90% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 143 | 153 | 183 |  | 0 | 0 | 0 | 1
3907011 |  |  | 3 | 90 | 70 | 11 | 11.5 | 0 | 26 | 30 | 41 | 837.08 | 1397.1862 | 1498.3321 | 1791.4 | 1.5 | 1.1 | 1.1 | 1.1 | 837 | 1397 | 1498 | 1791 | 72 | 120 | 129 | 154 | 0.043589 | 0.116 | 0.13329 | 0.18737 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 187.2108 | 200.7635 | 240.032 | 0.95 | 0.95 | 0.95 | 187 | 201 | 240 | 80 | 86 | 103 | 0.053323 | 0.061241 | 0.086531 | 0.9 | 5.5 | 5.9 | 7.9 |  | 1231 |  | 68% |  |  | 0 | 13.2 | 15.1 | 21.85 |  | 1 | 1 | 1 | 187 | 201 | 240 |  | 0 | 0 | 0 | 1
3907015 |  |  | 3 | 90 | 70 | 15 | 16.5 | 0 | 26 | 30 | 41.1 | 975.8274 | 1070.8274 | 1149.5095 | 1521.41 | 1.5 | 1.08 | 1.08 | 1.08 | 976 | 1071 | 1150 | 1521 | 84 | 92 | 99 | 131 | 0.03665 | 0.043823 | 0.050617 | 0.087813 | 0.0002083 | 1.724 | 2 | 0.00046183 | 135.0948 | 145.0213 | 191.94 | 1.01 | 1.01 | 1.01 | 135 | 145 | 192 | 58 | 62 | 83 | 0.017715 | 0.020191 | 0.035798 | 0.7 | 5.1 | 5.6 | 7.2 |  | 1484 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 135 | 145 | 192 |  | 0 | 0 | 0 | 1
3907016 |  |  | 3 | 90 | 70 | 16 | 16.5 | 0 | 26 | 30 | 41.1 | 1235.56 | 1627.6272 | 1747.2217 | 2312.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1236 | 1628 | 1747 | 2313 | 106 | 140 | 150 | 199 | 0.16745 | 0.29028 | 0.33273 | 0.58224 | 0.0002083 | 1.724 | 4 | 0.0013928 | 175.6782 | 188.5866 | 249.6 | 0.95 | 0.95 | 0.95 | 176 | 189 | 250 | 76 | 81 | 108 | 0.086774 | 0.098411 | 0.17375 | 1.4 | 5.1 | 5.6 | 7.2 |  | 1817 |  | 68% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 176 | 189 | 250 |  | 0 | 0 | 0 | 1
3907020 |  |  | 3 | 90 | 70 | 20 | 21.5 | 0 | 26 | 30 | 41.1 | 1414.8408 | 1509.8408 | 1619.1421 | 1935.84 | 1.5 | 1.08 | 1.08 | 1.08 | 1415 | 1510 | 1619 | 1936 | 122 | 130 | 139 | 166 | 0.060375 | 0.068444 | 0.078121 | 0.11095 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 170.5263 | 182.8711 | 218.64 | 0.95 | 0.95 | 0.95 | 171 | 183 | 219 | 74 | 79 | 94 | 0.022511 | 0.025609 | 0.036085 | 0.9 | 5.1 | 5.6 | 7.2 |  | 2070 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 171 | 183 | 219 |  | 0 | 0 | 0 | 1
3907021 |  |  | 3 | 90 | 70 | 21 | 21.5 | 0 | 26 | 30 | 41.1 | 1882.8292 | 1977.8292 | 2123.1559 | 2810.06 | 1.5 | 1.05 | 1.05 | 1.05 | 1883 | 1978 | 2123 | 2810 | 162 | 170 | 183 | 242 | 0.14998 | 0.1649 | 0.19063 | 0.33051 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 192.2437 | 206.3694 | 273.136 | 0.85 | 0.85 | 0.85 | 192 | 206 | 273 | 83 | 89 | 117 | 0.040321 | 0.046237 | 0.079107 | 1.9 | 5.1 | 5.6 | 7.2 |  | 2639 |  | 80% |  |  | 0 | 12.3 | 14.4 | 21.85 |  | 1 | 1 | 1 | 192 | 206 | 273 |  | 0 | 0 | 0 | 1
3908010 |  |  | 3 | 90 | 80 | 10 | 11.5 | 0 | 26 | 30 | 41.8 | 985.5 | 1214.227 | 1304.1434 | 1574.18 | 1.5 | 1.08 | 1.08 | 1.08 | 986 | 1214 | 1304 | 1574 | 85 | 104 | 112 | 135 | 0.03735 | 0.055029 | 0.063457 | 0.09091 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 168.3371 | 180.8029 | 218.24 | 0.98 | 0.98 | 0.98 | 168 | 181 | 218 | 72 | 78 | 94 | 0.027165 | 0.031672 | 0.045313 | 0.5 | 6.3 | 6.8 | 9.1 |  | 1095 |  | 90% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 168 | 181 | 218 |  | 0 | 0 | 0 | 1
3908011 |  |  | 3 | 90 | 80 | 11 | 11.5 | 0 | 26 | 30 | 41.8 | 956.08 | 1647.5037 | 1769.5053 | 2135.9 | 1.5 | 1.1 | 1.1 | 1.1 | 956 | 1648 | 1770 | 2136 | 82 | 142 | 152 | 184 | 0.059152 | 0.16872 | 0.19219 | 0.27712 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 220.8 | 236.8 | 286.4 | 0.95 | 0.95 | 0.95 | 221 | 237 | 286 | 95 | 102 | 123 | 0.078299 | 0.08967 | 0.1282 | 1.1 | 6.3 | 6.8 | 9.1 |  | 1406 |  | 68% |  |  | 0 | 12.8 | 14.7 | 21.85 |  | 1 | 1 | 1 | 221 | 237 | 286 |  | 0 | 0 | 0 | 1
3908015 |  |  | 3 | 90 | 80 | 15 | 16.5 | 0 | 26 | 30 | 42.4 | 1300.3374 | 1395.3374 | 1496.2563 | 2007.56 | 1.5 | 1.08 | 1.08 | 1.08 | 1300 | 1395 | 1496 | 2008 | 112 | 120 | 129 | 173 | 0.065908 | 0.075462 | 0.086971 | 0.15479 | 0.0002083 | 1.724 | 2 | 0.00046183 | 190.4692 | 204.245 | 274.04 | 1.01 | 1.01 | 1.01 | 190 | 204 | 274 | 82 | 88 | 118 | 0.035769 | 0.041076 | 0.073014 | 0.8 | 6 | 6.7 | 9 |  | 1696 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 190 | 204 | 274 |  | 0 | 0 | 0 | 1
3908016 |  |  | 3 | 90 | 80 | 16 | 16.5 | 0 | 26 | 30 | 42.4 | 1412.36 | 2040.4332 | 2188.0092 | 2935.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1412 | 2040 | 2188 | 2936 | 121 | 175 | 188 | 252 | 0.22071 | 0.45745 | 0.52704 | 0.94073 | 0.0002083 | 1.724 | 4 | 0.0013928 | 249.6 | 268 | 360 | 0.95 | 0.95 | 0.95 | 250 | 268 | 360 | 108 | 115 | 155 | 0.17637 | 0.19963 | 0.35992 | 1.6 | 6 | 6.7 | 9 |  | 2077 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 250 | 268 | 360 |  | 0 | 0 | 0 | 1
3908020 |  |  | 3 | 90 | 80 | 20 | 21.5 | 0 | 26 | 30 | 42.4 | 1847.5719 | 1942.5719 | 2086.4239 | 2518.44 | 1.5 | 1.08 | 1.08 | 1.08 | 1848 | 1943 | 2086 | 2518 | 159 | 167 | 179 | 217 | 0.10344 | 0.11396 | 0.13068 | 0.1911 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 240.0717 | 257.8495 | 311.24 | 0.95 | 0.95 | 0.95 | 240 | 258 | 311 | 103 | 111 | 134 | 0.043952 | 0.05093 | 0.073817 | 1.1 | 6 | 6.7 | 9 |  | 2366 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 240 | 258 | 311 |  | 0 | 0 | 0 | 1
3908021 |  |  | 3 | 90 | 80 | 21 | 21.5 | 0 | 26 | 30 | 42.4 | 2412.8 | 2627.7849 | 2817.8416 | 3780.76 | 1.5 | 1.05 | 1.05 | 1.05 | 2413 | 2628 | 2818 | 3781 | 208 | 226 | 242 | 325 | 0.25019 | 0.2945 | 0.33687 | 0.60165 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 272.6898 | 292.4123 | 392.336 | 0.85 | 0.85 | 0.85 | 273 | 292 | 392 | 117 | 126 | 169 | 0.080928 | 0.093575 | 0.16643 | 2.1 | 6 | 6.7 | 9 |  | 3016 |  | 80% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 273 | 292 | 392 |  | 0 | 0 | 0 | 1
3909010 |  |  | 3 | 90 | 90 | 10 | 11.5 | 0 | 26 | 30 | 42.4 | 1108.8 | 1395.6272 | 1501.3 | 1828.08 | 1.5 | 1.08 | 1.08 | 1.08 | 1109 | 1396 | 1501 | 1828 | 95 | 120 | 129 | 157 | 0.04834 | 0.075609 | 0.086853 | 0.12662 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 193.4859 | 208.1361 | 253.44 | 0.98 | 0.98 | 0.98 | 193 | 208 | 253 | 83 | 89 | 109 | 0.03734 | 0.042669 | 0.062889 | 0.6 | 6.7 | 7.4 | 10.3 |  | 1232 |  | 90% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 193 | 208 | 253 |  | 0 | 0 | 0 | 1
3909011 |  |  | 3 | 90 | 90 | 11 | 11.5 | 0 | 26 | 30 | 42.4 | 1075.76 | 1893.6336 | 2037.014 | 2480.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1076 | 1894 | 2037 | 2480 | 93 | 163 | 175 | 213 | 0.079227 | 0.23039 | 0.26382 | 0.38395 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 253.7304 | 272.9421 | 332.352 | 0.95 | 0.95 | 0.95 | 254 | 273 | 332 | 109 | 117 | 143 | 0.1071 | 0.12254 | 0.17952 | 1.2 | 6.7 | 7.4 | 10.3 |  | 1582 |  | 68% |  |  | 0 | 12.5 | 14.7 | 21.85 |  | 1 | 1 | 1 | 254 | 273 | 332 |  | 0 | 0 | 0 | 1
3909015 |  |  | 3 | 90 | 90 | 15 | 16.5 | 0 | 26 | 30 | 43.3 | 1502.9168 | 1597.9168 | 1711.9131 | 2331.36 | 1.5 | 1.08 | 1.08 | 1.08 | 1503 | 1598 | 1712 | 2331 | 129 | 137 | 147 | 200 | 0.088747 | 0.099847 | 0.11462 | 0.20964 | 0.0002083 | 1.724 | 2 | 0.00046183 | 218.1221 | 233.683 | 318.24 | 1.01 | 1.01 | 1.01 | 218 | 234 | 318 | 94 | 101 | 137 | 0.047774 | 0.054978 | 0.099847 | 0.9 | 7 | 7.7 | 10.7 |  | 1908 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 218 | 234 | 318 |  | 0 | 0 | 0 | 1
3909016 |  |  | 3 | 90 | 90 | 16 | 16.5 | 0 | 26 | 30 | 43.3 | 1588.48 | 2336.6695 | 2503.3688 | 3409.2 | 1.5 | 1.1 | 1.1 | 1.1 | 1588 | 2337 | 2503 | 3409 | 137 | 201 | 215 | 293 | 0.28598 | 0.60915 | 0.69575 | 1.2823 | 0.0002083 | 1.724 | 4 | 0.0013928 | 286.2235 | 306.6429 | 417.6 | 0.95 | 0.95 | 0.95 | 286 | 307 | 418 | 123 | 132 | 180 | 0.23125 | 0.26578 | 0.48995 | 1.8 | 7 | 7.7 | 10.7 |  | 2336 |  | 68% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 286 | 307 | 418 |  | 0 | 0 | 0 | 1
3909020 |  |  | 3 | 90 | 90 | 20 | 21.5 | 0 | 26 | 30 | 43.3 | 2128.8 | 2232.7837 | 2401.8435 | 2924.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2129 | 2233 | 2402 | 2925 | 183 | 192 | 207 | 252 | 0.13847 | 0.15221 | 0.17653 | 0.26018 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 275.9373 | 296.8305 | 361.44 | 0.95 | 0.95 | 0.95 | 276 | 297 | 361 | 119 | 128 | 155 | 0.059353 | 0.068506 | 0.099844 | 1.2 | 7 | 7.7 | 10.7 |  | 2661 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 276 | 297 | 361 |  | 0 | 0 | 0 | 1
3909021 |  |  | 3 | 90 | 90 | 21 | 21.5 | 0 | 26 | 30 | 43.3 | 2714.4 | 3009.2948 | 3223.9796 | 4390.56 | 1.5 | 1.05 | 1.05 | 1.05 | 2714 | 3009 | 3224 | 4391 | 233 | 259 | 277 | 378 | 0.31865 | 0.39212 | 0.44738 | 0.82373 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 312.2797 | 334.5579 | 455.616 | 0.85 | 0.85 | 0.85 | 312 | 335 | 456 | 134 | 144 | 196 | 0.10787 | 0.12418 | 0.22706 | 2.4 | 7 | 7.7 | 10.7 |  | 3393 |  | 80% |  |  | 0 | 11.3 | 13.2 | 21.85 |  | 1 | 1 | 1 | 312 | 335 | 456 |  | 0 | 0 | 0 | 1
39010010 |  |  | 3 | 90 | 100 | 10 | 11.5 | 0 | 26 | 30 | 43 | 1232.1 | 1574.3905 | 1696.1266 | 2081.98 | 1.5 | 1.08 | 1.08 | 1.08 | 1232 | 1574 | 1696 | 2082 | 106 | 135 | 146 | 179 | 0.062152 | 0.098623 | 0.11456 | 0.1692 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 218.2692 | 235.1463 | 288.64 | 0.98 | 0.98 | 0.98 | 218 | 235 | 289 | 94 | 101 | 124 | 0.049429 | 0.056681 | 0.083841 | 0.7 | 7.8 | 8.7 | 12.2 |  | 1369 |  | 90% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 218 | 235 | 289 |  | 0 | 0 | 0 | 1
39010011 |  |  | 3 | 90 | 100 | 11 | 11.5 | 0 | 26 | 30 | 43 | 1195.44 | 2136.1857 | 2301.3612 | 2824.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1195 | 2136 | 2301 | 2825 | 103 | 184 | 198 | 243 | 0.101 | 0.30352 | 0.34894 | 0.51536 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 286.4 | 308 | 378.4 | 0.95 | 0.95 | 0.95 | 286 | 308 | 378 | 123 | 132 | 163 | 0.14133 | 0.16156 | 0.24109 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1758 |  | 68% |  |  | 0 | 12.3 | 14.1 | 21.85 |  | 1 | 1 | 1 | 286 | 308 | 378 |  | 0 | 0 | 0 | 1
39010015 |  |  | 3 | 90 | 100 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1696 | 1798.7737 | 1926.0892 | 2655.16 | 1.5 | 1.08 | 1.08 | 1.08 | 1696 | 1799 | 1926 | 2655 | 146 | 155 | 166 | 228 | 0.1153 | 0.12961 | 0.14821 | 0.27587 | 0.0002083 | 1.724 | 2 | 0.00046183 | 245.5398 | 262.9189 | 362.44 | 1.01 | 1.01 | 1.01 | 246 | 263 | 362 | 106 | 113 | 156 | 0.061694 | 0.069895 | 0.13125 | 1 | 7 | 7.7 | 10.7 |  | 2120 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 246 | 263 | 362 |  | 0 | 0 | 0 | 1
39010016 |  |  | 3 | 90 | 100 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1765.28 | 2630.3871 | 2816.5634 | 3882.7 | 1.5 | 1.1 | 1.1 | 1.1 | 1765 | 2630 | 2817 | 3883 | 152 | 226 | 242 | 334 | 0.35572 | 0.77713 | 0.88934 | 1.6795 | 0.0002083 | 1.724 | 4 | 0.0013928 | 322.4 | 344.8 | 476 | 0.95 | 0.95 | 0.95 | 322 | 345 | 476 | 138 | 148 | 205 | 0.29411 | 0.33752 | 0.64121 | 2 | 7 | 7.7 | 10.7 |  | 2596 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 322 | 345 | 476 |  | 0 | 0 | 0 | 1
39010020 |  |  | 3 | 90 | 100 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2365.6 | 2518.7768 | 2713.5353 | 3330.84 | 1.5 | 1.08 | 1.08 | 1.08 | 2366 | 2519 | 2714 | 3331 | 203 | 217 | 233 | 286 | 0.17222 | 0.19638 | 0.22589 | 0.33822 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 311.2816 | 335.3507 | 411.64 | 0.95 | 0.95 | 0.95 | 311 | 335 | 412 | 134 | 144 | 177 | 0.076117 | 0.087677 | 0.13153 | 1.3 | 7 | 7.7 | 10.7 |  | 2957 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 311 | 335 | 412 |  | 0 | 0 | 0 | 1
39010021 |  |  | 3 | 90 | 100 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3016 | 3387.5609 | 3627.3291 | 5000.36 | 1.5 | 1.05 | 1.05 | 1.05 | 3016 | 3388 | 3627 | 5000 | 259 | 291 | 312 | 430 | 0.39928 | 0.50157 | 0.57492 | 1.0784 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 351.533 | 376.4142 | 518.896 | 0.85 | 0.85 | 0.85 | 352 | 376 | 519 | 151 | 162 | 223 | 0.13909 | 0.15955 | 0.29793 | 2.7 | 7 | 7.7 | 10.7 |  | 3770 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 352 | 376 | 519 |  | 0 | 0 | 0 | 1
39011010 |  |  | 3 | 90 | 110 | 10 | 11.5 | 0 | 26 | 30 | 43.5 | 1355.4 | 1766.3894 | 1902.9713 | 2335.88 | 1.5 | 1.08 | 1.08 | 1.08 | 1355 | 1766 | 1903 | 2336 | 117 | 152 | 164 | 201 | 0.078046 | 0.12847 | 0.1485 | 0.21898 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 244.8874 | 263.8227 | 323.84 | 0.98 | 0.98 | 0.98 | 245 | 264 | 324 | 105 | 114 | 139 | 0.063532 | 0.074284 | 0.10834 | 0.7 | 8.4 | 9.3 | 14 |  | 1506 |  | 90% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 245 | 264 | 324 |  | 0 | 0 | 0 | 1
39011011 |  |  | 3 | 90 | 110 | 11 | 11.5 | 0 | 26 | 30 | 43.5 | 1315.12 | 2396.6961 | 2582.015 | 3169.4 | 1.5 | 1.1 | 1.1 | 1.1 | 1315 | 2397 | 2582 | 3169 | 113 | 206 | 222 | 273 | 0.12603 | 0.39231 | 0.45212 | 0.6696 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 321.1364 | 345.9675 | 424.672 | 0.95 | 0.95 | 0.95 | 321 | 346 | 425 | 138 | 149 | 183 | 0.18379 | 0.21245 | 0.31347 | 1.5 | 8.4 | 9.3 | 14 |  | 1934 |  | 68% |  |  | 0 | 12 | 13.9 | 21.85 |  | 1 | 1 | 1 | 321 | 346 | 425 |  | 0 | 0 | 0 | 1
39011015 |  |  | 3 | 90 | 110 | 15 | 16.5 | 0 | 26 | 30 | 44.1 | 1813.1502 | 1908.1502 | 2043.2072 | 2816.61 | 1.5 | 1.08 | 1.08 | 1.08 | 1813 | 1908 | 2043 | 2817 | 156 | 164 | 176 | 242 | 0.13371 | 0.14742 | 0.16921 | 0.3153 | 0.0002083 | 1.724 | 2 | 0.00046183 | 249.8079 | 267.489 | 368.74 | 1.01 | 1.01 | 1.01 | 250 | 267 | 369 | 108 | 115 | 159 | 0.065294 | 0.073788 | 0.13878 | 1.1 | 7.9 | 8.8 | 12.5 |  | 2332 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 250 | 267 | 369 |  | 0 | 0 | 0 | 1
39011016 |  |  | 3 | 90 | 110 | 16 | 16.5 | 0 | 26 | 30 | 44.1 | 1942.08 | 2849.7498 | 3051.4523 | 4206.5 | 1.5 | 1.1 | 1.1 | 1.1 | 1942 | 2850 | 3051 | 4207 | 167 | 245 | 262 | 362 | 0.43368 | 0.92195 | 1.0522 | 1.9899 | 0.0002083 | 1.724 | 4 | 0.0013928 | 326.2664 | 349.3592 | 481.6 | 0.95 | 0.95 | 0.95 | 326 | 349 | 482 | 140 | 150 | 207 | 0.30664 | 0.35117 | 0.66163 | 2.2 | 7.9 | 8.8 | 12.5 |  | 2856 |  | 68% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 326 | 349 | 482 |  | 0 | 0 | 0 | 1
39011020 |  |  | 3 | 90 | 110 | 20 | 21.5 | 0 | 26 | 30 | 44.1 | 2597.5513 | 2692.5513 | 2900.7465 | 3560.64 | 1.5 | 1.08 | 1.08 | 1.08 | 2598 | 2693 | 2901 | 3561 | 223 | 232 | 249 | 306 | 0.20997 | 0.22695 | 0.26079 | 0.39117 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 317.18 | 341.7052 | 419.44 | 0.95 | 0.95 | 0.95 | 317 | 342 | 419 | 136 | 147 | 180 | 0.079545 | 0.092651 | 0.13786 | 1.5 | 7.9 | 8.8 | 12.5 |  | 3253 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 317 | 342 | 419 |  | 0 | 0 | 0 | 1
39011021 |  |  | 3 | 90 | 110 | 21 | 21.5 | 0 | 26 | 30 | 44.1 | 3317.6 | 3556.1815 | 3807.8846 | 5249.26 | 1.5 | 1.05 | 1.05 | 1.05 | 3318 | 3556 | 3808 | 5249 | 285 | 306 | 327 | 451 | 0.48995 | 0.563 | 0.64102 | 1.2027 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 356.5192 | 381.7533 | 526.256 | 0.85 | 0.85 | 0.85 | 357 | 382 | 526 | 154 | 164 | 226 | 0.14745 | 0.16667 | 0.31147 | 2.9 | 7.9 | 8.8 | 12.5 |  | 4147 |  | 80% |  |  | 0 | 10.9 | 12.8 | 21.85 |  | 1 | 1 | 1 | 357 | 382 | 526 |  | 0 | 0 | 0 | 1
39012010 |  |  | 3 | 90 | 120 | 10 | 11.5 | 0 | 26 | 30 | 44 | 1478.7 | 1924.9914 | 2079.6202 | 2589.78 | 1.5 | 1.08 | 1.08 | 1.08 | 1479 | 1925 | 2080 | 2590 | 127 | 166 | 179 | 223 | 0.094696 | 0.15749 | 0.18178 | 0.27629 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 266.8755 | 288.3128 | 359.04 | 0.98 | 0.98 | 0.98 | 267 | 288 | 359 | 115 | 124 | 154 | 0.078448 | 0.090498 | 0.13655 | 0.8 | 8.9 | 9.9 | 14.8 |  | 1643 |  | 90% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 267 | 288 | 359 |  | 0 | 0 | 0 | 1
39012011 |  |  | 3 | 90 | 120 | 11 | 11.5 | 0 | 26 | 30 | 44 | 1434.8 | 2611.8926 | 2821.6982 | 3513.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1435 | 2612 | 2822 | 3514 | 123 | 225 | 243 | 302 | 0.15445 | 0.48249 | 0.55812 | 0.84249 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 349.6 | 378.4 | 471.2 | 0.95 | 0.95 | 0.95 | 350 | 378 | 471 | 151 | 163 | 203 | 0.22724 | 0.26248 | 0.3972 | 1.6 | 8.9 | 9.9 | 14.8 |  | 2110 |  | 68% |  |  | 0 | 11.8 | 13.7 | 21.85 |  | 1 | 1 | 1 | 350 | 378 | 471 |  | 0 | 0 | 0 | 1
39012015 |  |  | 3 | 90 | 120 | 15 | 16.5 | 0 | 26 | 30 | 44.8 | 2035.2 | 2216.9074 | 2373.9949 | 3302.76 | 1.5 | 1.08 | 1.08 | 1.08 | 2035 | 2217 | 2374 | 3303 | 175 | 191 | 204 | 284 | 0.17035 | 0.20202 | 0.22969 | 0.43818 | 0.0002083 | 1.724 | 2 | 0.00046183 | 302.6168 | 324.0598 | 450.84 | 1.01 | 1.01 | 1.01 | 303 | 324 | 451 | 130 | 139 | 194 | 0.095501 | 0.10878 | 0.20825 | 1.2 | 8.7 | 9.8 | 14.3 |  | 2544 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 303 | 324 | 451 |  | 0 | 0 | 0 | 1
39012016 |  |  | 3 | 90 | 120 | 16 | 16.5 | 0 | 26 | 30 | 44.8 | 2118.2 | 3241.8334 | 3471.546 | 4829.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2118 | 3242 | 3472 | 4830 | 182 | 279 | 299 | 415 | 0.52004 | 1.2043 | 1.3801 | 2.6321 | 0.0002083 | 1.724 | 4 | 0.0013928 | 396.8 | 425.6 | 592 | 0.95 | 0.95 | 0.95 | 397 | 426 | 592 | 171 | 183 | 255 | 0.46012 | 0.52567 | 1.009 | 2.4 | 8.7 | 9.8 | 14.3 |  | 3115 |  | 68% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 397 | 426 | 592 |  | 0 | 0 | 0 | 1
39012020 |  |  | 3 | 90 | 120 | 20 | 21.5 | 0 | 26 | 30 | 44.8 | 2838.4 | 3079.683 | 3327.0648 | 4143.24 | 1.5 | 1.08 | 1.08 | 1.08 | 2838 | 3080 | 3327 | 4143 | 244 | 265 | 286 | 356 | 0.25382 | 0.29848 | 0.3467 | 0.53309 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 380.6009 | 411.1734 | 512.04 | 0.95 | 0.95 | 0.95 | 381 | 411 | 512 | 164 | 177 | 220 | 0.11647 | 0.13524 | 0.20716 | 1.6 | 8.7 | 9.8 | 14.3 |  | 3548 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 381 | 411 | 512 |  | 0 | 0 | 0 | 1
39012021 |  |  | 3 | 90 | 120 | 21 | 21.5 | 0 | 26 | 30 | 44.8 | 3619.2 | 4175.0158 | 4470.8527 | 6219.96 | 1.5 | 1.05 | 1.05 | 1.05 | 3619 | 4175 | 4471 | 6220 | 311 | 359 | 385 | 535 | 0.59093 | 0.78201 | 0.89645 | 1.7058 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 433.2486 | 463.9481 | 645.456 | 0.85 | 0.85 | 0.85 | 433 | 464 | 645 | 186 | 200 | 277 | 0.21706 | 0.24998 | 0.47147 | 3.2 | 8.7 | 9.8 | 14.3 |  | 4524 |  | 80% |  |  | 0 | 10.6 | 12.5 | 21.85 |  | 1 | 1 | 1 | 433 | 464 | 645 |  | 0 | 0 | 0 | 1
39014010 |  |  | 3 | 90 | 140 | 10 | 11.5 | 0 | 26 | 30 | 44.8 | 1725.3 | 2267.7915 | 2456.1428 | 3097.58 | 1.5 | 1.08 | 1.08 | 1.08 | 1725 | 2268 | 2456 | 3098 | 148 | 195 | 211 | 266 | 0.13567 | 0.22856 | 0.26538 | 0.4118 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 314.4004 | 340.5129 | 429.44 | 0.98 | 0.98 | 0.98 | 314 | 341 | 429 | 135 | 147 | 184 | 0.11405 | 0.13394 | 0.20477 | 0.9 | 10.1 | 11.2 | 17.5 |  | 1917 |  | 90% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 314 | 341 | 429 |  | 0 | 0 | 0 | 1
39014011 |  |  | 3 | 90 | 140 | 11 | 11.5 | 0 | 26 | 30 | 44.8 | 1673.48 | 3077.0153 | 3332.5766 | 4202.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1673 | 3077 | 3333 | 4203 | 144 | 265 | 287 | 361 | 0.22506 | 0.70735 | 0.822 | 1.267 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 412 | 446.4 | 563.2 | 0.95 | 0.95 | 0.95 | 412 | 446 | 563 | 177 | 192 | 242 | 0.33131 | 0.38594 | 0.59624 | 1.9 | 10.1 | 11.2 | 17.5 |  | 2461 |  | 68% |  |  | 0 | 11.5 | 13.3 | 21.85 |  | 1 | 1 | 1 | 412 | 446 | 563 |  | 0 | 0 | 0 | 1
39014015 |  |  | 3 | 90 | 140 | 15 | 16.5 | 0 | 26 | 30 | 45.4 | 2374.4 | 2628.9846 | 2815.4585 | 3950.36 | 1.5 | 1.08 | 1.08 | 1.08 | 2374 | 2629 | 2815 | 3950 | 204 | 226 | 242 | 340 | 0.23753 | 0.28984 | 0.33107 | 0.64183 | 0.0002083 | 1.724 | 2 | 0.00046183 | 358.867 | 384.3214 | 539.24 | 1.01 | 1.01 | 1.01 | 359 | 384 | 539 | 154 | 165 | 232 | 0.13762 | 0.15733 | 0.30498 | 1.4 | 9.6 | 10.5 | 16.1 |  | 2968 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 359 | 384 | 539 |  | 0 | 0 | 0 | 1
39014016 |  |  | 3 | 90 | 140 | 16 | 16.5 | 0 | 26 | 30 | 45.4 | 2471.12 | 3844.4231 | 4117.108 | 5776.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2471 | 3844 | 4117 | 5777 | 213 | 331 | 354 | 497 | 0.72521 | 1.722 | 1.9648 | 3.8281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 471.2 | 504 | 708 | 0.95 | 0.95 | 0.95 | 471 | 504 | 708 | 203 | 217 | 304 | 0.66 | 0.75214 | 1.4571 | 2.8 | 9.6 | 10.5 | 16.1 |  | 3634 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 471 | 504 | 708 |  | 0 | 0 | 0 | 1
39014020 |  |  | 3 | 90 | 140 | 20 | 21.5 | 0 | 26 | 30 | 45.4 | 3312 | 3628.1092 | 3929.4416 | 4955.64 | 1.5 | 1.08 | 1.08 | 1.08 | 3312 | 3628 | 3929 | 4956 | 285 | 312 | 338 | 426 | 0.35276 | 0.42119 | 0.49271 | 0.77564 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 448.3778 | 485.6178 | 612.44 | 0.95 | 0.95 | 0.95 | 448 | 486 | 612 | 193 | 209 | 263 | 0.16455 | 0.19227 | 0.30142 | 1.9 | 9.6 | 10.5 | 16.1 |  | 4140 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 448 | 486 | 612 |  | 0 | 0 | 0 | 1
39014021 |  |  | 3 | 90 | 140 | 21 | 21.5 | 0 | 26 | 30 | 45.4 | 4222.4 | 4951.0649 | 5302.2439 | 7439.56 | 1.5 | 1.05 | 1.05 | 1.05 | 4222 | 4951 | 5302 | 7440 | 363 | 426 | 456 | 640 | 0.82471 | 1.1262 | 1.2858 | 2.4907 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 513.7806 | 550.223 | 772.016 | 0.85 | 0.85 | 0.85 | 514 | 550 | 772 | 221 | 237 | 332 | 0.3145 | 0.36017 | 0.69325 | 3.7 | 9.6 | 10.5 | 16.1 |  | 5278 |  | 80% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 514 | 550 | 772 |  | 0 | 0 | 0 | 1
39016010 |  |  | 3 | 90 | 160 | 10 | 11.5 | 0 | 26 | 30 | 45.5 | 1971 | 2603.9362 | 2826.6988 | 3605.38 | 1.5 | 1.08 | 1.08 | 1.08 | 1971 | 2604 | 2827 | 3605 | 170 | 224 | 243 | 310 | 0.1878 | 0.31579 | 0.36823 | 0.58343 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 361.0026 | 391.8858 | 499.84 | 0.98 | 0.98 | 0.98 | 361 | 392 | 500 | 155 | 169 | 215 | 0.15785 | 0.18573 | 0.29229 | 1.1 | 11 | 12.4 | 19.2 |  | 2190 |  | 90% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 361 | 392 | 500 |  | 0 | 0 | 0 | 1
39016011 |  |  | 3 | 90 | 160 | 11 | 11.5 | 0 | 26 | 30 | 45.5 | 1912.84 | 3533.1076 | 3835.3593 | 4891.9 | 1.5 | 1.1 | 1.1 | 1.1 | 1913 | 3533 | 3835 | 4892 | 165 | 304 | 330 | 421 | 0.31229 | 0.97923 | 1.1422 | 1.8051 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 473.6 | 513.6 | 655.2 | 0.95 | 0.95 | 0.95 | 474 | 514 | 655 | 204 | 221 | 282 | 0.46405 | 0.53894 | 0.85059 | 2.1 | 11 | 12.4 | 19.2 |  | 2813 |  | 68% |  |  | 0 | 11.2 | 13 | 21.85 |  | 1 | 1 | 1 | 474 | 514 | 655 |  | 0 | 0 | 0 | 1
39016015 |  |  | 3 | 90 | 160 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 2713.6 | 3021.1784 | 3225.612 | 4597.96 | 1.5 | 1.08 | 1.08 | 1.08 | 2714 | 3021 | 3226 | 4598 | 233 | 260 | 277 | 395 | 0.31739 | 0.39255 | 0.44386 | 0.88425 | 0.0002083 | 1.724 | 2 | 0.00046183 | 412.403 | 440.309 | 627.64 | 1.01 | 1.01 | 1.01 | 412 | 440 | 628 | 177 | 189 | 270 | 0.18642 | 0.21164 | 0.42236 | 1.6 | 11.5 | 12.8 | 19.6 |  | 3392 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 412 | 440 | 628 |  | 0 | 0 | 0 | 1
39016016 |  |  | 3 | 90 | 160 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 2824.72 | 4417.9369 | 4716.8848 | 6723.7 | 1.5 | 1.1 | 1.1 | 1.1 | 2825 | 4418 | 4717 | 6724 | 243 | 380 | 406 | 578 | 0.96013 | 2.3042 | 2.6234 | 5.2466 | 0.0002083 | 1.724 | 4 | 0.0013928 | 540.8 | 577.6 | 824 | 0.95 | 0.95 | 0.95 | 541 | 578 | 824 | 233 | 249 | 354 | 0.88438 | 1.007 | 2.0053 | 3.2 | 11.5 | 12.8 | 19.6 |  | 4154 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 541 | 578 | 824 |  | 0 | 0 | 0 | 1
39016020 |  |  | 3 | 90 | 160 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 3784.8 | 4165.8877 | 4522.2728 | 5768.04 | 1.5 | 1.08 | 1.08 | 1.08 | 3785 | 4166 | 4522 | 5768 | 326 | 358 | 389 | 496 | 0.46965 | 0.56398 | 0.66342 | 1.0674 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 514.8389 | 558.8826 | 712.84 | 0.95 | 0.95 | 0.95 | 515 | 559 | 713 | 221 | 240 | 307 | 0.2199 | 0.25827 | 0.41766 | 2.1 | 11.5 | 12.8 | 19.6 |  | 4731 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 515 | 559 | 713 |  | 0 | 0 | 0 | 1
39016021 |  |  | 3 | 90 | 160 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 4825.6 | 5689.6682 | 6074.6702 | 8659.16 | 1.5 | 1.05 | 1.05 | 1.05 | 4826 | 5690 | 6075 | 8659 | 415 | 489 | 522 | 745 | 1.1025 | 1.5162 | 1.7213 | 3.4394 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 590.4267 | 630.379 | 898.576 | 0.85 | 0.85 | 0.85 | 590 | 630 | 899 | 254 | 271 | 387 | 0.42584 | 0.4827 | 0.96272 | 4.3 | 11.5 | 12.8 | 19.6 |  | 6032 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 590 | 630 | 899 |  | 0 | 0 | 0 | 1
39018010 |  |  | 3 | 90 | 180 | 10 | 11.5 | 0 | 26 | 30 | 46 | 2217.6 | 2970.6878 | 3224.8254 | 4113.18 | 1.5 | 1.08 | 1.08 | 1.08 | 2218 | 2971 | 3225 | 4113 | 191 | 256 | 277 | 354 | 0.24793 | 0.42972 | 0.49841 | 0.79115 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 411.848 | 447.081 | 570.24 | 0.98 | 0.98 | 0.98 | 412 | 447 | 570 | 177 | 192 | 245 | 0.21496 | 0.25037 | 0.39566 | 1.2 | 12.2 | 13.7 | 22 |  | 2464 |  | 90% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 412 | 447 | 570 |  | 0 | 0 | 0 | 1
39018011 |  |  | 3 | 90 | 180 | 11 | 11.5 | 0 | 26 | 30 | 46 | 2151.52 | 4030.7284 | 4375.5508 | 5580.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2152 | 4031 | 4376 | 5581 | 185 | 347 | 376 | 480 | 0.41325 | 1.3345 | 1.5507 | 2.4499 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 540.0825 | 586.2857 | 747.792 | 0.95 | 0.95 | 0.95 | 540 | 586 | 748 | 232 | 252 | 322 | 0.62966 | 0.73454 | 1.1605 | 2.4 | 12.2 | 13.7 | 22 |  | 3164 |  | 68% |  |  | 0 | 10.9 | 12.7 | 21.85 |  | 1 | 1 | 1 | 540 | 586 | 748 |  | 0 | 0 | 0 | 1
39018015 |  |  | 3 | 90 | 180 | 15 | 16.5 | 0 | 26 | 30 | 46.4 | 3052.8 | 3233.3461 | 3452.1364 | 4920.86 | 1.5 | 1.08 | 1.08 | 1.08 | 3053 | 3233 | 3452 | 4921 | 263 | 278 | 297 | 423 | 0.41352 | 0.46033 | 0.52312 | 1.0378 | 0.0002083 | 1.724 | 2 | 0.00046183 | 420.6821 | 449.1483 | 640.24 | 1.01 | 1.01 | 1.01 | 421 | 449 | 640 | 181 | 193 | 275 | 0.20103 | 0.22751 | 0.45077 | 1.8 | 11.5 | 12.8 | 19.6 |  | 3816 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 421 | 449 | 640 |  | 0 | 0 | 0 | 1
39018016 |  |  | 3 | 90 | 180 | 16 | 16.5 | 0 | 26 | 30 | 46.4 | 3177.64 | 4843.455 | 5171.1964 | 7371.3 | 1.5 | 1.1 | 1.1 | 1.1 | 3178 | 4843 | 5171 | 7371 | 273 | 417 | 445 | 634 | 1.2316 | 2.8183 | 3.2004 | 6.4023 | 0.0002083 | 1.724 | 4 | 0.0013928 | 549.0471 | 586.1994 | 835.6 | 0.95 | 0.95 | 0.95 | 549 | 586 | 836 | 236 | 252 | 359 | 0.92692 | 1.0535 | 2.1027 | 3.6 | 11.5 | 12.8 | 19.6 |  | 4673 |  | 68% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 549 | 586 | 836 |  | 0 | 0 | 0 | 1
39018020 |  |  | 3 | 90 | 180 | 20 | 21.5 | 0 | 26 | 30 | 46.4 | 4258.4 | 4497.8275 | 4882.6095 | 6227.64 | 1.5 | 1.08 | 1.08 | 1.08 | 4258 | 4498 | 4883 | 6228 | 366 | 387 | 420 | 536 | 0.60186 | 0.67106 | 0.78724 | 1.2676 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 526.1058 | 571.1133 | 728.44 | 0.95 | 0.95 | 0.95 | 526 | 571 | 728 | 226 | 246 | 313 | 0.23536 | 0.27757 | 0.44366 | 2.4 | 11.5 | 12.8 | 19.6 |  | 5323 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 526 | 571 | 728 |  | 0 | 0 | 0 | 1
39018021 |  |  | 3 | 90 | 180 | 21 | 21.5 | 0 | 26 | 30 | 46.4 | 5428.8 | 6016.7573 | 6423.8924 | 9156.96 | 1.5 | 1.05 | 1.05 | 1.05 | 5429 | 6017 | 6424 | 9157 | 467 | 517 | 552 | 788 | 1.4259 | 1.7365 | 1.9715 | 3.9339 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 600.0988 | 640.7056 | 913.296 | 0.85 | 0.85 | 0.85 | 600 | 641 | 913 | 258 | 276 | 393 | 0.45312 | 0.51605 | 1.0212 | 4.8 | 11.5 | 12.8 | 19.6 |  | 6786 |  | 80% |  |  | 0 | 10 | 11.8 | 21.85 |  | 1 | 1 | 1 | 600 | 641 | 913 |  | 0 | 0 | 0 | 1
39020010 |  |  | 3 | 90 | 200 | 10 | 11.5 | 0 | 26 | 30 | 46.5 | 2464.2 | 3259.5786 | 3552.8678 | 4620.98 | 1.5 | 1.08 | 1.08 | 1.08 | 2464 | 3260 | 3553 | 4621 | 212 | 280 | 306 | 397 | 0.31839 | 0.53596 | 0.63306 | 1.0323 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 451.899 | 492.5599 | 640.64 | 0.98 | 0.98 | 0.98 | 452 | 493 | 641 | 194 | 212 | 276 | 0.26975 | 0.31839 | 0.5217 | 1.3 | 13.4 | 14.8 | 24 |  | 2738 |  | 90% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 452 | 493 | 641 |  | 0 | 0 | 0 | 1
39020011 |  |  | 3 | 90 | 200 | 11 | 11.5 | 0 | 26 | 30 | 46.5 | 2390.88 | 4422.7051 | 4820.6497 | 6269.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2391 | 4423 | 4821 | 6270 | 206 | 380 | 415 | 539 | 0.53681 | 1.6745 | 1.9735 | 3.2154 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 592.8 | 645.6 | 840 | 0.95 | 0.95 | 0.95 | 593 | 646 | 840 | 255 | 278 | 361 | 0.79741 | 0.93613 | 1.5219 | 2.7 | 13.4 | 14.8 | 24 |  | 3516 |  | 68% |  |  | 0 | 10.7 | 12.5 | 21.85 |  | 1 | 1 | 1 | 593 | 646 | 840 |  | 0 | 0 | 0 | 1
39020015 |  |  | 3 | 90 | 200 | 15 | 16.5 | 0 | 26 | 30 | 47.1 | 3392 | 3875.4624 | 4083.4736 | 5893.16 | 1.5 | 1.08 | 1.08 | 1.08 | 3392 | 3875 | 4083 | 5893 | 292 | 333 | 351 | 507 | 0.52075 | 0.671 | 0.74279 | 1.5125 | 0.0002083 | 1.724 | 2 | 0.00046183 | 529.0162 | 557.4105 | 804.44 | 1.01 | 1.01 | 1.01 | 529 | 557 | 804 | 227 | 240 | 346 | 0.32058 | 0.35686 | 0.7225 | 2 | 13.2 | 14.7 | 23.5 |  | 4240 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 529 | 557 | 804 |  | 0 | 0 | 0 | 1
39020016 |  |  | 3 | 90 | 200 | 16 | 16.5 | 0 | 26 | 30 | 47.1 | 3530.56 | 5667.1756 | 5971.3549 | 8617.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3531 | 5667 | 5971 | 8618 | 304 | 487 | 514 | 741 | 1.5505 | 3.8886 | 4.321 | 8.8378 | 0.0002083 | 1.724 | 4 | 0.0013928 | 694.4 | 731.2 | 1056 | 0.95 | 0.95 | 0.95 | 694 | 731 | 1056 | 298 | 314 | 454 | 1.4914 | 1.6515 | 3.3905 | 4 | 13.2 | 14.7 | 23.5 |  | 5192 |  | 68% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 694 | 731 | 1056 |  | 0 | 0 | 0 | 1
39020020 |  |  | 3 | 90 | 200 | 20 | 21.5 | 0 | 26 | 30 | 47.1 | 4731.2 | 5214.8122 | 5684.0287 | 7392.84 | 1.5 | 1.08 | 1.08 | 1.08 | 4731 | 5215 | 5684 | 7393 | 407 | 448 | 489 | 636 | 0.75597 | 0.91133 | 1.0809 | 1.8048 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 644.4696 | 702.4575 | 913.64 | 0.95 | 0.95 | 0.95 | 644 | 702 | 914 | 277 | 302 | 393 | 0.35773 | 0.42311 | 0.70617 | 2.7 | 13.2 | 14.7 | 23.5 |  | 5914 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 644 | 702 | 914 |  | 0 | 0 | 0 | 1
39020021 |  |  | 3 | 90 | 200 | 21 | 21.5 | 0 | 26 | 30 | 47.1 | 6032 | 7298.5083 | 7690.2476 | 11098.36 | 1.5 | 1.05 | 1.05 | 1.05 | 6032 | 7299 | 7690 | 11098 | 519 | 628 | 661 | 954 | 1.7969 | 2.5976 | 2.8682 | 5.8399 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 757.3788 | 798.0303 | 1151.696 | 0.85 | 0.85 | 0.85 | 757 | 798 | 1152 | 326 | 343 | 495 | 0.73289 | 0.80825 | 1.6398 | 5.3 | 13.2 | 14.7 | 23.5 |  | 7540 |  | 80% |  |  | 0 | 10 | 11.4 | 21.85 |  | 1 | 1 | 1 | 757 | 798 | 1152 |  | 0 | 0 | 0 | 1
39022010 |  |  | 3 | 90 | 220 | 10 | 11.5 | 0 | 26 | 30 | 46.9 | 2710.8 | 3560.7045 | 3890.5075 | 5128.78 | 1.5 | 1.08 | 1.08 | 1.08 | 2711 | 3561 | 3891 | 5129 | 233 | 306 | 335 | 441 | 0.39979 | 0.66495 | 0.78763 | 1.3182 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 493.6463 | 539.3693 | 711.04 | 0.98 | 0.98 | 0.98 | 494 | 539 | 711 | 212 | 232 | 306 | 0.33527 | 0.3966 | 0.66495 | 1.5 | 13.4 | 14.8 | 24 |  | 3012 |  | 90% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 494 | 539 | 711 |  | 0 | 0 | 0 | 1
39022011 |  |  | 3 | 90 | 220 | 11 | 11.5 | 0 | 26 | 30 | 46.9 | 2630.24 | 4831.2828 | 5278.7706 | 6958.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2630 | 4831 | 5279 | 6959 | 226 | 415 | 454 | 598 | 0.6751 | 2.0817 | 2.46 | 4.1089 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 647.3498 | 707.3093 | 932.432 | 0.95 | 0.95 | 0.95 | 647 | 707 | 932 | 278 | 304 | 401 | 0.99013 | 1.1684 | 1.9531 | 2.9 | 13.4 | 14.8 | 24 |  | 3868 |  | 68% |  |  | 0 | 10.5 | 12.3 | 21.85 |  | 1 | 1 | 1 | 647 | 707 | 932 |  | 0 | 0 | 0 | 1
39022015 |  |  | 3 | 90 | 220 | 15 | 16.5 | 0 | 26 | 30 | 47.8 | 3731.2 | 4302.5567 | 4481.7989 | 6540.76 | 1.5 | 1.08 | 1.08 | 1.08 | 3731 | 4303 | 4482 | 6541 | 321 | 370 | 385 | 563 | 0.64222 | 0.84427 | 0.91146 | 1.8979 | 0.0002083 | 1.724 | 2 | 0.00046183 | 587.3163 | 611.7835 | 892.84 | 1.01 | 1.01 | 1.01 | 587 | 612 | 893 | 252 | 263 | 384 | 0.40329 | 0.43778 | 0.9069 | 2.2 | 15.5 | 16.8 | 27.5 |  | 4664 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 587 | 612 | 893 |  | 0 | 0 | 0 | 1
39022016 |  |  | 3 | 90 | 220 | 16 | 16.5 | 0 | 26 | 30 | 47.8 | 3883.48 | 6291.7252 | 6553.835 | 9564.7 | 1.5 | 1.1 | 1.1 | 1.1 | 3883 | 6292 | 6554 | 9565 | 334 | 541 | 564 | 823 | 1.8993 | 4.8599 | 5.2712 | 11.0281 | 0.0002083 | 1.724 | 4 | 0.0013928 | 770.6865 | 802.7929 | 1171.6 | 0.95 | 0.95 | 0.95 | 771 | 803 | 1172 | 332 | 345 | 504 | 1.8773 | 2.0229 | 4.2327 | 4.4 | 15.5 | 16.8 | 27.5 |  | 5711 |  | 68% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 771 | 803 | 1172 |  | 0 | 0 | 0 | 1
39022020 |  |  | 3 | 90 | 220 | 20 | 21.5 | 0 | 26 | 30 | 47.8 | 5204 | 5696.5662 | 6224.1991 | 8205.24 | 1.5 | 1.08 | 1.08 | 1.08 | 5204 | 5697 | 6224 | 8205 | 448 | 490 | 535 | 706 | 0.92971 | 1.1066 | 1.3129 | 2.2531 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 704.007 | 769.2142 | 1014.04 | 0.95 | 0.95 | 0.95 | 704 | 769 | 1014 | 303 | 331 | 436 | 0.43521 | 0.51657 | 0.88193 | 2.9 | 15.5 | 16.8 | 27.5 |  | 6505 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 704 | 769 | 1014 |  | 0 | 0 | 0 | 1
39022021 |  |  | 3 | 90 | 220 | 21 | 21.5 | 0 | 26 | 30 | 47.8 | 6635.2 | 8102.8385 | 8440.3982 | 12317.96 | 1.5 | 1.05 | 1.05 | 1.05 | 6635 | 8103 | 8440 | 12318 | 571 | 697 | 726 | 1059 | 2.2168 | 3.257 | 3.5238 | 7.3137 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 840.8456 | 875.8747 | 1278.256 | 0.85 | 0.85 | 0.85 | 841 | 876 | 1278 | 362 | 377 | 550 | 0.92217 | 0.99699 | 2.0624 | 5.9 | 15.5 | 16.8 | 27.5 |  | 8294 |  | 80% |  |  | 0 | 10 | 11.1 | 21.85 |  | 1 | 1 | 1 | 841 | 876 | 1278 |  | 0 | 0 | 0 | 1
39024010 |  |  | 3 | 90 | 240 | 10 | 11.5 | 0 | 26 | 30 | 47.2 | 2957.4 | 3860.4189 | 4228.9856 | 5636.58 | 1.5 | 1.08 | 1.08 | 1.08 | 2957 | 3860 | 4229 | 5637 | 254 | 332 | 364 | 485 | 0.49269 | 0.81123 | 0.96313 | 1.6466 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 535.1979 | 586.295 | 781.44 | 0.98 | 0.98 | 0.98 | 535 | 586 | 781 | 230 | 252 | 336 | 0.40968 | 0.4855 | 0.82955 | 1.6 | 14.8 | 16.6 | 28 |  | 3286 |  | 90% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 535 | 586 | 781 |  | 0 | 0 | 0 | 1
39024011 |  |  | 3 | 90 | 240 | 11 | 11.5 | 0 | 26 | 30 | 47.2 | 2868.92 | 5237.9453 | 5738.0289 | 7647.9 | 1.5 | 1.1 | 1.1 | 1.1 | 2869 | 5238 | 5738 | 7648 | 247 | 450 | 493 | 658 | 0.83958 | 2.5443 | 3.0135 | 5.1519 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 701.6 | 768.8 | 1024.8 | 0.95 | 0.95 | 0.95 | 702 | 769 | 1025 | 302 | 331 | 441 | 1.2166 | 1.4411 | 2.4508 | 3.2 | 14.8 | 16.6 | 28 |  | 4219 |  | 68% |  |  | 0 | 10.4 | 12.2 | 21.85 |  | 1 | 1 | 1 | 702 | 769 | 1025 |  | 0 | 0 | 0 | 1
39024015 |  |  | 3 | 90 | 240 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4070.4 | 4729.7153 | 4901.7743 | 7188.36 | 1.5 | 1.08 | 1.08 | 1.08 | 4070 | 4730 | 4902 | 7188 | 350 | 407 | 422 | 618 | 0.77843 | 1.0403 | 1.1153 | 2.3255 | 0.0002083 | 1.724 | 2 | 0.00046183 | 645.6251 | 669.1119 | 981.24 | 1.01 | 1.01 | 1.01 | 646 | 669 | 981 | 278 | 288 | 422 | 0.50038 | 0.53546 | 1.1153 | 2.4 | 16.4 | 17.7 | 29.7 |  | 5088 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 646 | 669 | 981 |  | 0 | 0 | 0 | 1
39024016 |  |  | 3 | 90 | 240 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4236.4 | 6916.3687 | 7167.9745 | 10511.7 | 1.5 | 1.1 | 1.1 | 1.1 | 4236 | 6916 | 7168 | 10512 | 364 | 595 | 616 | 904 | 2.2878 | 5.9506 | 6.3666 | 13.4546 | 0.0002083 | 1.724 | 4 | 0.0013928 | 847.2 | 878.4 | 1288 | 0.95 | 0.95 | 0.95 | 847 | 878 | 1288 | 364 | 378 | 554 | 2.2878 | 2.4619 | 5.1781 | 4.8 | 16.4 | 17.7 | 29.7 |  | 6230 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 847 | 878 | 1288 |  | 0 | 0 | 0 | 1
39024020 |  |  | 3 | 90 | 240 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 5677.6 | 6176.062 | 6765.7107 | 9017.64 | 1.5 | 1.08 | 1.08 | 1.08 | 5678 | 6176 | 6766 | 9018 | 488 | 531 | 582 | 776 | 1.1192 | 1.3185 | 1.5755 | 2.7565 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 763.2652 | 836.1366 | 1114.44 | 0.95 | 0.95 | 0.95 | 763 | 836 | 1114 | 328 | 359 | 479 | 0.51828 | 0.61727 | 1.0795 | 3.2 | 16.4 | 17.7 | 29.7 |  | 7097 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 763 | 836 | 1114 |  | 0 | 0 | 0 | 1
39024021 |  |  | 3 | 90 | 240 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7238.4 | 8907.2896 | 9231.3218 | 13537.56 | 1.5 | 1.05 | 1.05 | 1.05 | 7238 | 8907 | 9231 | 13538 | 622 | 766 | 794 | 1164 | 2.6792 | 4.0011 | 4.2878 | 8.9741 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 924.3248 | 957.9502 | 1404.816 | 0.85 | 0.85 | 0.85 | 924 | 958 | 1405 | 397 | 412 | 604 | 1.131 | 1.2143 | 2.532 | 6.4 | 16.4 | 17.7 | 29.7 |  | 9048 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 924 | 958 | 1405 |  | 0 | 0 | 0 | 1
39026010 |  |  | 3 | 90 | 260 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3203.1 | 4178.1784 | 4608.285 | 6144.38 | 1.5 | 1.08 | 1.08 | 1.08 | 3203 | 4178 | 4608 | 6144 | 275 | 359 | 396 | 528 | 0.59766 | 0.98066 | 1.1771 | 2.0125 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 579.2512 | 638.88 | 851.84 | 0.98 | 0.98 | 0.98 | 579 | 639 | 852 | 249 | 275 | 366 | 0.49712 | 0.59766 | 1.0165 | 1.7 | 16.2 | 18.6 | 31.4 |  | 3559 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 579 | 639 | 852 |  | 0 | 0 | 0 | 1
39026011 |  |  | 3 | 90 | 260 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3108.28 | 5669.092 | 6252.675 | 8336.9 | 1.5 | 1.1 | 1.1 | 1.1 | 3108 | 5669 | 6253 | 8337 | 267 | 488 | 538 | 717 | 1.0195 | 3.1003 | 3.7135 | 6.324 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 759.609 | 837.804 | 1117.072 | 0.95 | 0.95 | 0.95 | 760 | 838 | 1117 | 327 | 360 | 480 | 1.4807 | 1.7678 | 3.007 | 3.5 | 16.2 | 18.6 | 31.4 |  | 4571 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 760 | 838 | 1117 |  | 0 | 0 | 0 | 1
39026015 |  |  | 3 | 90 | 260 | 15 | 16.5 | 0 | 26 | 30 | 48.1 | 4409.6 | 4942.1733 | 5121.9619 | 7511.26 | 1.5 | 1.08 | 1.08 | 1.08 | 4410 | 4942 | 5122 | 7511 | 379 | 425 | 440 | 646 | 0.92984 | 1.1583 | 1.238 | 2.5902 | 0.0002083 | 1.724 | 2 | 0.00046183 | 653.9155 | 677.704 | 993.84 | 1.01 | 1.01 | 1.01 | 654 | 678 | 994 | 281 | 292 | 427 | 0.52438 | 0.56434 | 1.1688 | 2.6 | 16.4 | 17.7 | 29.7 |  | 5512 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 654 | 678 | 994 |  | 0 | 0 | 0 | 1
39026016 |  |  | 3 | 90 | 260 | 16 | 16.5 | 0 | 26 | 30 | 48.1 | 4590 | 7342.4692 | 7609.5768 | 11159.3 | 1.5 | 1.1 | 1.1 | 1.1 | 4590 | 7342 | 7610 | 11159 | 395 | 631 | 654 | 960 | 2.7305 | 6.7819 | 7.2711 | 15.3567 | 0.0002083 | 1.724 | 4 | 0.0013928 | 855.096 | 886.2031 | 1299.6 | 0.95 | 0.95 | 0.95 | 855 | 886 | 1300 | 368 | 381 | 559 | 2.3802 | 2.5459 | 5.3585 | 5.2 | 16.4 | 17.7 | 29.7 |  | 6750 |  | 68% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 855 | 886 | 1300 |  | 0 | 0 | 0 | 1
39026020 |  |  | 3 | 90 | 260 | 20 | 21.5 | 0 | 26 | 30 | 48.1 | 6150.4 | 6444.5232 | 7107.93 | 9477.24 | 1.5 | 1.08 | 1.08 | 1.08 | 6150 | 6445 | 7108 | 9477 | 529 | 554 | 611 | 815 | 1.3333 | 1.4581 | 1.763 | 3.084 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 768.4272 | 847.53 | 1130.04 | 0.95 | 0.95 | 0.95 | 768 | 848 | 1130 | 330 | 365 | 486 | 0.53527 | 0.65032 | 1.1314 | 3.5 | 16.4 | 17.7 | 29.7 |  | 7688 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 768 | 848 | 1130 |  | 0 | 0 | 0 | 1
39026021 |  |  | 3 | 90 | 260 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 7841.6 | 9234.8264 | 9570.7751 | 14035.36 | 1.5 | 1.05 | 1.05 | 1.05 | 7842 | 9235 | 9571 | 14035 | 674 | 794 | 823 | 1207 | 3.2013 | 4.3863 | 4.6996 | 9.8288 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 934.0101 | 967.988 | 1419.536 | 0.85 | 0.85 | 0.85 | 934 | 968 | 1420 | 402 | 416 | 611 | 1.189 | 1.2694 | 2.6515 | 6.9 | 16.4 | 17.7 | 29.7 |  | 9802 |  | 80% |  |  | 0 | 10 | 10.9 | 21.85 |  | 1 | 1 | 1 | 934 | 968 | 1420 |  | 0 | 0 | 0 | 1
39028010 |  |  | 3 | 90 | 280 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3449.7 | 4331.3824 | 4782.2249 | 6369.68 | 1.5 | 1.08 | 1.08 | 1.08 | 3450 | 4331 | 4782 | 6370 | 297 | 372 | 411 | 548 | 0.71972 | 1.0925 | 1.3147 | 2.2448 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 587.6832 | 648.8536 | 864.24 | 0.98 | 0.98 | 0.98 | 588 | 649 | 864 | 253 | 279 | 372 | 0.53495 | 0.64106 | 1.0925 | 1.9 | 16.2 | 18.6 | 31.4 |  | 3833 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 588 | 649 | 864 |  | 0 | 0 | 0 | 1
39028011 |  |  | 3 | 90 | 280 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3346.96 | 5976.86 | 6598.9761 | 8789.5 | 1.5 | 1.1 | 1.1 | 1.1 | 3347 | 5977 | 6599 | 8790 | 288 | 514 | 568 | 756 | 1.2293 | 3.5696 | 4.2925 | 7.2837 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 764.8 | 844.8 | 1124.8 | 0.95 | 0.95 | 0.95 | 765 | 845 | 1125 | 329 | 363 | 484 | 1.5697 | 1.8808 | 3.1948 | 3.7 | 16.2 | 18.6 | 31.4 |  | 4922 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 765 | 845 | 1125 |  | 0 | 0 | 0 | 1
39028015 |  |  | 3 | 90 | 280 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 4748.8 | 5583.9636 | 5708.9475 | 8483.56 | 1.5 | 1.08 | 1.08 | 1.08 | 4749 | 5584 | 5709 | 8484 | 408 | 480 | 491 | 730 | 1.0969 | 1.4974 | 1.5638 | 3.3484 | 0.0002083 | 1.724 | 2 | 0.00046183 | 762.2334 | 779.2943 | 1158.04 | 1.01 | 1.01 | 1.01 | 762 | 779 | 1158 | 328 | 335 | 498 | 0.72271 | 0.75246 | 1.6068 | 2.8 | 19.3 | 20.4 | 34.5 |  | 5936 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 762 | 779 | 1158 |  | 0 | 0 | 0 | 1
39028016 |  |  | 3 | 90 | 280 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 4942.92 | 8165.5551 | 8348.322 | 12405.7 | 1.5 | 1.1 | 1.1 | 1.1 | 4943 | 8166 | 8348 | 12406 | 425 | 702 | 718 | 1067 | 3.2026 | 8.4775 | 8.857 | 19.1435 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1000 | 1022.4 | 1520 | 0.95 | 0.95 | 0.95 | 1000 | 1022 | 1520 | 430 | 439 | 654 | 3.2759 | 3.41 | 7.3878 | 5.6 | 19.3 | 20.4 | 34.5 |  | 7269 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1000 | 1022 | 1520 |  | 0 | 0 | 0 | 1
39028020 |  |  | 3 | 90 | 280 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 6624 | 7236.8592 | 7990.1254 | 10642.44 | 1.5 | 1.08 | 1.08 | 1.08 | 6624 | 7237 | 7990 | 10642 | 570 | 622 | 687 | 915 | 1.5687 | 1.8574 | 2.2516 | 3.9249 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 894.3632 | 987.4552 | 1315.24 | 0.95 | 0.95 | 0.95 | 894 | 987 | 1315 | 384 | 424 | 565 | 0.73142 | 0.88554 | 1.5422 | 3.7 | 19.3 | 20.4 | 34.5 |  | 8280 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 894 | 987 | 1315 |  | 0 | 0 | 0 | 1
39028021 |  |  | 3 | 90 | 280 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 8444.8 | 10516.0623 | 10751.4398 | 15976.76 | 1.5 | 1.05 | 1.05 | 1.05 | 8445 | 10516 | 10751 | 15977 | 726 | 904 | 925 | 1374 | 3.777 | 5.7534 | 6.0129 | 12.8758 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1009.4247 | 1032.0183 | 1533.5908 | 0.85 | 0.85 | 0.85 | 1009 | 1032 | 1534 | 434 | 444 | 660 | 1.4114 | 1.4741 | 3.1464 | 7.5 | 19.3 | 20.4 | 34.5 |  | 10556 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1009 | 1032 | 1534 |  | 0 | 0 | 0 | 1
39030010 |  |  | 3 | 90 | 300 | 10 | 11.5 | 0 | 26 | 30 | 47.8 | 3696.3 | 4485 | 4951 | 6595 | 1.5 | 1.08 | 1.08 | 1.08 | 3696 | 4485 | 4951 | 6595 | 318 | 386 | 426 | 567 | 0.85091 | 1.2178 | 1.4618 | 2.4849 | 0.0003969 | 1.7346 | 2 | 0.00036735 | 595 | 658 | 877 | 0.98 | 0.98 | 0.98 | 595 | 658 | 877 | 256 | 283 | 377 | 0.57015 | 0.68603 | 1.1657 | 2 | 16.2 | 18.6 | 31.4 |  | 4107 |  | 90% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 595 | 658 | 877 |  | 0 | 0 | 0 | 1
39030011 |  |  | 3 | 90 | 300 | 11 | 11.5 | 0 | 26 | 30 | 47.8 | 3586.32 | 6285 | 6939 | 9242 | 1.5 | 1.1 | 1.1 | 1.1 | 3586 | 6285 | 6939 | 9242 | 308 | 541 | 597 | 795 | 1.4551 | 4.0948 | 4.9094 | 8.3291 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 770.4 | 850.4 | 1132.8 | 0.95 | 0.95 | 0.95 | 770 | 850 | 1133 | 331 | 366 | 487 | 1.6604 | 1.9965 | 3.3742 | 4 | 16.2 | 18.6 | 31.4 |  | 5274 |  | 68% |  |  | 0 | 10.2 | 11.9 | 21.85 |  | 1 | 1 | 1 | 770 | 850 | 1133 |  | 0 | 0 | 0 | 1
39030015 |  |  | 3 | 90 | 300 | 15 | 16.5 | 0 | 26 | 30 | 48.9 | 5088 | 5796 | 5926 | 8806 | 1.5 | 1.08 | 1.08 | 1.08 | 5088 | 5796 | 5926 | 8806 | 438 | 498 | 510 | 757 | 1.2857 | 1.6433 | 1.7199 | 3.6657 | 0.0002083 | 1.724 | 2 | 0.00046183 | 771 | 788 | 1171 | 1.01 | 1.01 | 1.01 | 771 | 788 | 1171 | 332 | 339 | 504 | 0.75777 | 0.78851 | 1.6814 | 3 | 19.3 | 20.4 | 34.5 |  | 6360 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 771 | 788 | 1171 |  | 0 | 0 | 0 | 1
39030016 |  |  | 3 | 90 | 300 | 16 | 16.5 | 0 | 26 | 30 | 48.9 | 5295.84 | 8592 | 8784 | 13053 | 1.5 | 1.1 | 1.1 | 1.1 | 5296 | 8592 | 8784 | 13053 | 455 | 739 | 755 | 1123 | 3.7173 | 9.5114 | 9.9151 | 21.4461 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1008 | 1030.4 | 1532 | 0.95 | 0.95 | 0.95 | 1008 | 1030 | 1532 | 433 | 443 | 659 | 3.3777 | 3.5301 | 7.6161 | 6 | 19.3 | 20.4 | 34.5 |  | 7788 |  | 68% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1008 | 1030 | 1532 |  | 0 | 0 | 0 | 1
39030020 |  |  | 3 | 90 | 300 | 20 | 21.5 | 0 | 26 | 30 | 48.9 | 7096.8 | 7549 | 8335 | 11102 | 1.5 | 1.08 | 1.08 | 1.08 | 7097 | 7549 | 8335 | 11102 | 610 | 649 | 717 | 955 | 1.8199 | 2.0515 | 2.4873 | 4.3324 | 0.0001276 | 1.7219 | 2 | 0.00037661 | 905 | 999 | 1331 | 0.95 | 0.95 | 0.95 | 905 | 999 | 1331 | 389 | 430 | 572 | 0.76432 | 0.92701 | 1.6074 | 4 | 19.3 | 20.4 | 34.5 |  | 8871 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 905 | 999 | 1331 |  | 0 | 0 | 0 | 1
39030021 |  |  | 3 | 90 | 300 | 21 | 21.5 | 0 | 26 | 30 | 48.1 | 9048 | 10844 | 11086 | 16475 | 1.5 | 1.05 | 1.05 | 1.05 | 9048 | 10844 | 11086 | 16475 | 778 | 933 | 953 | 1417 | 4.408 | 6.2432 | 6.5023 | 13.9308 | 0.0001276 | 1.7219 | 4 | 0.0005142 | 1174.4 | 1200.8 | 1784.8 | 0.85 | 0.85 | 0.85 | 1174 | 1201 | 1785 | 505 | 516 | 768 | 1.9303 | 2.0113 | 4.3002 | 8 | 19.3 | 20.4 | 34.5 |  | 11310 |  | 80% |  |  | 0 | 10 | 10.6 | 21.85 |  | 1 | 1 | 1 | 1174 | 1201 | 1785 |  | 0 | 0 | 0 | 1
5285111 |  |  | 5 | 28 | 51 | 11 | 13 | 0 | 26 | 30 | 41 | 1553 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 1553 | 1648 | 1770 | 2136 | 134 | 142 | 152 | 184 | 0.12893 | 0.1443 | 0.16471 | 0.23885 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 106.9244 | 125.0304 | 0.95 | 0.95 | 0.95 | 276 | 107 | 125 | 119 | 46 | 54 | 0.10238 | 0.016271 | 0.022172 | 0.7 | 0 | 0 | 0 |  | 99999 |  | 68% | [7 empty] | 1 | 1 | 1 | 276 | 107 | 125 |  | 0 | 0 | 0 | 1
5285116 |  |  | 5 | 28 | 51 | 16 | 18 | 0 | 26 | 30 |  | 1945 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 1945 | 2040 | 2188 | 2936 | 167 | 175 | 188 | 252 | 0.40096 | 0.44001 | 0.50732 | 0.90805 | 0.0002083 | 1.724 | 4 | 0.0013928 | 163.7931 | 175.2709 | 204.9504 | 0.95 | 0.95 | 0.95 | 164 | 175 | 205 | 71 | 75 | 88 | 0.073452 | 0.081884 | 0.11243 | 1 | 0 | 0 | 0 |  | 99999 |  | 68% | [7 empty] | 1 | 1 | 1 | 164 | 175 | 205 |  | 0 | 0 | 0 | 1
5288111 |  |  | 5 | 28 | 81 | 11 | 13 | 0 | 26 | 30 | 41.8 | 592.28 | 1648 | 1770 | 2136 | 1.5 | 1.1 | 1.1 | 1.1 | 592 | 1648 | 1770 | 2136 | 51 | 142 | 152 | 184 | 0.024131 | 0.16956 | 0.19314 | 0.27844 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 276 | 296 | 358 | 0.95 | 0.95 | 0.95 | 276 | 296 | 358 | 119 | 127 | 154 | 0.12097 | 0.13698 | 0.19803 | 1.1 | 6.3 | 6.8 | 9.1 |  | 871 |  | 68% | [7 empty] | 1 | 1 | 1 | 276 | 296 | 358 |  | 0 | 0 | 0 | 1
5288116 |  |  | 5 | 28 | 81 | 16 | 18 | 0 | 26 | 30 | 42.4 | 779.28 | 2040 | 2188 | 2936 | 1.5 | 1.1 | 1.1 | 1.1 | 779 | 2040 | 2188 | 2936 | 67 | 175 | 188 | 252 | 0.068921 | 0.45805 | 0.52772 | 0.94186 | 0.0002083 | 1.724 | 4 | 0.0013928 | 312 | 335 | 450 | 0.95 | 0.95 | 0.95 | 312 | 335 | 450 | 134 | 144 | 194 | 0.27036 | 0.31164 | 0.56153 | 1.6 | 6 | 6.7 | 9 |  | 1146 |  | 68% | [7 empty] | 1 | 1 | 1 | 312 | 335 | 450 |  | 0 | 0 | 0 | 1
52810111 |  |  | 5 | 28 | 101 | 11 | 13 | 0 | 26 | 30 | 43 | 740.52 | 2136 | 2301 | 2825 | 1.5 | 1.1 | 1.1 | 1.1 | 741 | 2136 | 2301 | 2825 | 64 | 184 | 198 | 243 | 0.041354 | 0.30484 | 0.35044 | 0.51749 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 358 | 385 | 473 | 0.95 | 0.95 | 0.95 | 358 | 385 | 473 | 154 | 166 | 203 | 0.21741 | 0.25069 | 0.36747 | 1.3 | 7.8 | 8.7 | 12.2 |  | 1089 |  | 68% | [7 empty] | 1 | 1 | 1 | 358 | 385 | 473 |  | 0 | 0 | 0 | 1
52810116 |  |  | 5 | 28 | 101 | 16 | 18 | 0 | 26 | 30 | 44.1 | 974.44 | 2630 | 2817 | 3883 | 1.5 | 1.1 | 1.1 | 1.1 | 974 | 2630 | 2817 | 3883 | 84 | 226 | 242 | 334 | 0.111 | 0.77806 | 0.89039 | 1.6813 | 0.0002083 | 1.724 | 4 | 0.0013928 | 403 | 431 | 595 | 0.95 | 0.95 | 0.95 | 403 | 431 | 595 | 173 | 185 | 256 | 0.45955 | 0.52444 | 0.99483 | 2 | 7 | 7.7 | 10.7 |  | 1433 |  | 68% | [7 empty] | 1 | 1 | 1 | 403 | 431 | 595 |  | 0 | 0 | 0 | 1
52812111 |  |  | 5 | 28 | 121 | 11 | 13 | 0 | 26 | 30 | 44 | 888.76 | 2612 | 2822 | 3514 | 1.5 | 1.1 | 1.1 | 1.1 | 889 | 2612 | 2822 | 3514 | 76 | 225 | 243 | 302 | 0.062859 | 0.48436 | 0.56026 | 0.84561 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 437 | 473 | 589 | 0.95 | 0.95 | 0.95 | 437 | 473 | 589 | 188 | 203 | 253 | 0.34496 | 0.39877 | 0.60469 | 1.6 | 8.9 | 9.9 | 14.8 |  | 1307 |  | 68% | [7 empty] | 1 | 1 | 1 | 437 | 473 | 589 |  | 0 | 0 | 0 | 1
52812116 |  |  | 5 | 28 | 121 | 16 | 18 | 0 | 26 | 30 | 44.8 | 1169.6 | 3242 | 3472 | 4830 | 1.5 | 1.1 | 1.1 | 1.1 | 1170 | 3242 | 3472 | 4830 | 101 | 279 | 299 | 415 | 0.16408 | 1.2057 | 1.3816 | 2.6347 | 0.0002083 | 1.724 | 4 | 0.0013928 | 496 | 532 | 740 | 0.95 | 0.95 | 0.95 | 496 | 532 | 740 | 213 | 229 | 318 | 0.70918 | 0.81767 | 1.5597 | 2.4 | 8.7 | 9.8 | 14.3 |  | 1720 |  | 68% | [7 empty] | 1 | 1 | 1 | 496 | 532 | 740 |  | 0 | 0 | 0 | 1
52814111 |  |  | 5 | 28 | 141 | 11 | 13 | 0 | 26 | 30 | 44.8 | 1037 | 3077 | 3333 | 4203 | 1.5 | 1.1 | 1.1 | 1.1 | 1037 | 3077 | 3333 | 4203 | 89 | 265 | 287 | 361 | 0.091983 | 0.70983 | 0.82485 | 1.2713 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 515 | 558 | 704 | 0.95 | 0.95 | 0.95 | 515 | 558 | 704 | 221 | 240 | 303 | 0.50448 | 0.58909 | 0.91363 | 1.9 | 10.1 | 11.2 | 17.5 |  | 1525 |  | 68% | [7 empty] | 1 | 1 | 1 | 515 | 558 | 704 |  | 0 | 0 | 0 | 1
52814116 |  |  | 5 | 28 | 141 | 16 | 18 | 0 | 26 | 30 | 45.4 | 1364.08 | 3844 | 4117 | 5777 | 1.5 | 1.1 | 1.1 | 1.1 | 1364 | 3844 | 4117 | 5777 | 117 | 331 | 354 | 497 | 0.22486 | 1.7238 | 1.9669 | 3.8317 | 0.0002083 | 1.724 | 4 | 0.0013928 | 589 | 630 | 885 | 0.95 | 0.95 | 0.95 | 589 | 630 | 885 | 253 | 271 | 381 | 1.0174 | 1.1642 | 2.2724 | 2.8 | 9.6 | 10.5 | 14.4 |  | 2006 |  | 68% | [7 empty] | 1 | 1 | 1 | 589 | 630 | 885 |  | 0 | 0 | 0 | 1
52818111 |  |  | 5 | 28 | 181 | 11 | 13 | 0 | 26 | 30 | 46 | 1332.8 | 4031 | 4376 | 5581 | 1.5 | 1.1 | 1.1 | 1.1 | 1333 | 4031 | 4376 | 5581 | 115 | 347 | 376 | 480 | 0.17173 | 1.3385 | 1.5552 | 2.4569 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 675 | 733 | 935 | 0.95 | 0.95 | 0.95 | 675 | 733 | 935 | 290 | 315 | 402 | 0.9574 | 1.1172 | 1.7625 | 2.4 | 12.2 | 13.7 | 22 |  | 1960 |  | 68% | [7 empty] | 1 | 1 | 1 | 675 | 733 | 935 |  | 0 | 0 | 0 | 1
52818116 |  |  | 5 | 28 | 181 | 16 | 18 | 0 | 26 | 30 | 46.4 | 1753.72 | 4843 | 5171 | 7371 | 1.5 | 1.1 | 1.1 | 1.1 | 1754 | 4843 | 5171 | 7371 | 151 | 417 | 445 | 634 | 0.38888 | 2.821 | 3.2034 | 6.4079 | 0.0002083 | 1.724 | 4 | 0.0013928 | 686 | 733 | 1045 | 0.95 | 0.95 | 0.95 | 686 | 733 | 1045 | 295 | 315 | 449 | 1.4342 | 1.6303 | 3.26 | 3.6 | 11.5 | 12.8 | 19.6 |  | 2579 |  | 68% | [7 empty] | 1 | 1 | 1 | 686 | 733 | 1045 |  | 0 | 0 | 0 | 1
52824111 |  |  | 5 | 28 | 241 | 11 | 13 | 0 | 26 | 30 | 47.2 | 1777.52 | 5238 | 5738 | 7648 | 1.5 | 1.1 | 1.1 | 1.1 | 1778 | 5238 | 5738 | 7648 | 153 | 450 | 493 | 658 | 0.34891 | 2.5506 | 3.0208 | 5.164 | 0.0003969 | 1.7346 | 4 | 0.00057429 | 877 | 961 | 1281 | 0.95 | 0.95 | 0.95 | 877 | 961 | 1281 | 377 | 413 | 551 | 1.8378 | 2.1757 | 3.7133 | 3.2 | 14.8 | 16.6 | 28 |  | 2614 |  | 68% | [7 empty] | 1 | 1 | 1 | 877 | 961 | 1281 |  | 0 | 0 | 0 | 1
52824116 |  |  | 5 | 28 | 241 | 16 | 18 | 0 | 26 | 30 | 48.1 | 2338.52 | 6916 | 7168 | 10512 | 1.5 | 1.1 | 1.1 | 1.1 | 2339 | 6916 | 7168 | 10512 | 201 | 595 | 616 | 904 | 0.72441 | 5.9555 | 6.3719 | 13.4648 | 0.0002083 | 1.724 | 4 | 0.0013928 | 1059 | 1098 | 1610 | 0.95 | 0.95 | 0.95 | 1059 | 1098 | 1610 | 455 | 472 | 692 | 3.5331 | 3.7944 | 7.9936 | 4.8 | 16.4 | 17.7 | 29.7 |  | 3439 |  | 68% | [7 empty] | 1 | 1 | 1 | 1059 | 1098 | 1610 |  | 0 | 0 | 0 | 1
Note on D4: Thomas Henson: Strada = 1 Linea = 2 Tempo = 3 Built_in = 4
∆𝑝= 𝑘_1∗𝑞^𝑛∗((𝐿−144)∗𝑡)/1000+𝑘_2∗𝑞^2
SI-eenheden
Imperiale-eenheden

## NL (hidden)
Selectiontool Strada Hybrid
| Lengte |  | mm | Invulformulier | Statisch toestel | rel. vocht. | Unit | Kopieer alle data
| Hoogte |  | mm | Uitvoering | Hybrid toestel | Eenheidsstelsel | DBH set | SI-eenheden
| Type |  |  | Temperaturen | DBH rail type | Toestel |  | Imperiale-eenheden
| Diepte |  | mm | Indien de ventilatoren uitgeschakeld zijn, is de afgifte een indicatieve waarde. | Waterzijdig drukverlies
| Verwarmen: |  |  |  |  | Koelen:
| Water aanvoer |  |  | Water aanvoer |  |  |  | 0
| Water retour |  | 0 | Water retour |  |  |  | 0
| Ruimte (droge bol) |  | 0 | Ruimte (droge bol) |  |  |  | 0
|  | Verwarmen: // |  | Koelen: // |  | Watervolume | Elektrisch verbruik [W] | Geluidsdrukniveau [dB(A)]**** | Geluidsvermogen [dB(A)]****
|  | Verwarmvermogen | Waterdebiet | Koelvermogen | Waterdebiet
Statisch (indicatieve waarde)
EN16430 | Ventilatorsnelheid
Ventilatorsnelheid 2
Ventilatorsnelheid 3
Stuurspanning [v]
* | Koelvermogen is berekend volgens EN16430 met de ventilatoren naar boven blazend voor alle types.
** | Wanneer het watervolume in gallons wordt gegeven, zijn dit imperial gallons.
*** | Geluidsvermogen volgens ISO 3741:2010, Voor het geluidsdrukniveau is er een aangenomen kamerdemping van 8 dB(A).

## EN (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## FR (hidden)
Selectiontool Strada Hybrid
| Longeur |  | mm | Formulaire | Appareil statique | hum. rel. | Unité | Copier toutes des données
| Hauteur |  | mm | Version | Appareil Hybrid | Système unitaire | DBH set | Unités-SI
| Type |  |  | Températures | DBH rail type | Appareil |  | Unités-Impériales
| Profondeur |  | mm | Si les ventilateurs sont éteints, la sortie est une valeur indicative. | Perte de charge
| Chauffer: |  |  |  |  | Refroidir:
| Entrée de l'eau |  |  | Entrée de l'eau |  |  |  | 0
| Retour de l'eau |  | 0 | Retour de l'eau |  |  |  | 0
| Ambiante (bulbe sec) |  | 0 | Ambiante (bulbe sec) |  |  |  | 0
|  | Chauffer: // |  | Refroidir: // |  | Volume d'eau | Puissance absorbée elec. [W] | Pression sonore [dB(A)]**** | Puissance sonore [dB(A)]****
|  | Puissance de chauffer | Débit d'eau | Puissance de refroidir | Débit d'eau
Ventilateur éteint (indicative)
EN16430 | Vitesse ventilateur
Vitesse du ventilateur 2
Vitesse du ventilateur 3
Tension ventilateur [V]
* | La puissance de refroidissement est calculée selon EN 16430 avec des ventilateurs qui soufflent pour toutes les hauteurs.
** | Lorsque le volume d'eau est donné en gallons, ce sont des gallons impérial.
*** | Puissance acoustique selon ISO 3741: 2010, niveau de pression acoustique avec un amortissement de la pièce supposé de 8 dB(A).

## DE (hidden)
Selectiontool Strada Hybrid
| Länge |  | mm | Eingabefelder | Statisches Gerät | rel. Luftf. | Unit | Kopieren Sie alle daten
| Höhe |  | mm | Ausführung | Hybrid Gerät | Einheiten | DBH set | SI-einheiten
| Typ |  |  | Temperaturen | DBH rail typ | Gerät |  | Imperiale-einheiten
| Tiefe |  | mm | Wenn die Lüfter ausgeschaltet sind, ist der Ausgang ein Richtwert. | zug. wassers. Druckverlust
| Heizen: |  |  |  |  | Kühlen:
| Vorlauf wasser |  |  | Vorlauf wasser |  |  |  | 0
| Rücklauf wasser |  | 0 | Rücklauf wasser |  |  |  | 0
| Raum (trocken) |  | 0 | Raum (trocken) |  |  |  | 0
|  | Heizen: // |  | Kühlen: // |  | Wasservolumen | Elektr. Leistung [W] | Schalldruckpegel [dB(A)]**** | Schallleistungspegel [dB(A)]****
|  | Heizleistung | Heizmittelstrom | Kühlleistung | Kühlmittelstrom
Lüfter aus (richtwert)
EN16430 | Auslegungsstufe
Auslegungsstufe 2
Auslegungsstufe 3
Lufterspannung [V]
* | Die Kühlleistung wird nach EN 16430 berechnet, wobei die Lüfter für alle Höhen hochgehen.
** | Wenn das Wasservolumen in Gallonen angegeben ist, sind dies imperiale Gallonen.
*** | Schallleistung nach ISO 3741: 2010, Schalldruckpegel bei angenommener Raumdämpfung von 8 dB(A).

## NR (hidden)
Selectiontool Strada Hybrid
| Lengde |  | mm | Inngangsskjema | Statisk modell | rel. fuktighet | Unit | Kopier alle data
| Høyde |  | mm | Versjon | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Type |  |  | Temperaturer | DBH rail type | Modell |  | Imperiale-enheter
| Bredde |  | mm | Hvis viftene er slått av, er utgangen en indikativ verdi. | Trykktap
| Varme: |  |  |  |  | Kjøling:
| Tur vann |  |  | Tur vann |  |  |  | 0
| Retur vann |  | 0 | Retur vann |  |  |  | 0
| Rom (tørr pære) |  | 0 | Rom (tørr pære) |  |  |  | 0
|  | Varme: // |  | Kjøling: // |  | Vannvolum | Elektrisk effekt [W] | Lydtrykk [dB(A)]**** | Lydeffekt [dB(A)]****
|  | Varme effekt | Vannmengde | Kjøle effekt | Vannmengde
Lüfter aus (richtwert)
EN16430 | Styresignal
Auslegungsstufe 2
Auslegungsstufe 3
Viftespenning [V]
* | Kjølekapasitet beregnes i henhold til EN16430 med viftene som blåser oppover for alle typer.
** | Når vannvolumet er gitt i gallon, er dette imperial gallons.
*** | Lydeffekt i henhold til ISO 3741: 2010. For lydtrykknivået er det en antatt romdemping på 8 dB (A).

## SP (hidden)
Selectiontool Strada Hybrid
| Longitud |  | mm | Formulary | Dispositivo estático | Hum. Relativa | Unit | Copiar todos los datos
| Altura |  | mm | Versión | Dispositivo Hybrid | Convers. de unidades | DBH set | Unidades-SI
| Tipo |  |  | Temperaturas | tipo de riel DBH | Despositivo |  | Unidades-Imperial
| Profund. |  | mm | La velocidad del ventilador en "0" tiene una emisión indicativa. | Pérdida de carga del agua
| Calefacción: |  |  |  |  | Enfriamiento:
| Agua impulsión |  |  | Agua impulsión |  |  |  | 0
| Agua retorno |  | 0 | Agua retorno |  |  |  | 0
| Ambiente (bulbo seco) |  | 0 | Ambiente (bulbo seco) |  |  |  | 0
|  | Calefacción: // |  | Enfriamiento: // |  | Volumen de agua | Potencia eléctrica absorbida [W] | Presión sonora [dB(A)]**** | Potencia sonora [dB(A)]****
|  | Emisión calefacción | Caudal de agua, calefacción | Emisión sensible Frío | Caudal de agua, calefacción
Fans off (indicative value)
EN16430 | Velocidad del ventilador
Fan speed selection 2
Fan speed selection 3
Voltaje control [V]
* | La potencia de enfriamiento se calcula según la norma EN 16430 con ventiladores de todas las alturas.
** | Cuando el volumen de agua se da en galones, las unidades son específicamente galones imperiales.
*** | Potencia sonora según ISO 3741: 2010, nivel de presión acústica con una amortiguación ambiental supuesta de 8 dB (A).

## SW (hidden)
Selectiontool Strada Hybrid
| Längd |  | mm | Inngangsskjema | Statisk modell | rel. Fuktighet | Unit | Kopiera all data
| Höjd |  | mm | Storlek | Hybrid modell | Enhetssystem | DBH set | SI-enheter
| Typ |  |  | Temperaturer | DBH rail typ | Modell |  | Imperiella-enheter
| Djup |  | mm | Om fläktarna är avstängda är utgången ett indikationsvärde. | Tryckfall, vatten
| Värme: |  |  |  |  | Kyla:
| Tillopp |  |  | Tillopp |  |  |  | 0
| Retur |  | 0 | Retur |  |  |  | 0
| Rum (torr) |  | 0 | Rum (torr) |  |  |  | 0
|  | Värme: // |  | Kyla: // |  | Vattenvolym | Effektförbrukning [W] | Ljudtryck [dB(A)]**** | Ljudeffekt [dB(A)]****
|  | Effekt | Vattenflöde | Kyleffekt | Vattenflöde
Fans off (indicative value)
EN16430 | Fläkthastighet
Fan speed selection 2
Fan speed selection 3
Spänning, Fläkt [V]
* | Kyleffekt är beräknad enligt EN16430 med fläktar blåsandes i riktning uppåt för alla höjder
** | När vattenvolymen är given i gallon avser det Imperiella gallon.
*** | Ljudeffekt enligt ISO 3741:2010 ljudtryck med antagen ljudreduktion från rummet på 8 dB(A)

## TS (hidden)
Selectiontool Strada Hybrid
| Délka |  | mm | Formulary | Statická jednotka | Relativní vlhkost | Jednotka | Kopírovat všechna data
| Výška |  | mm | Verze | Hybridní jednotka | Převod jednotek | DBH sada | Mezinárodní (Sl)
| Typ |  |  | Teploty | DBH rail type | Device |  | Imperiální
| Hloubka |  | mm | Pokud jsou ventilátory vypnuté, je výkon pouze orientační. | Tlaková ztráta
| Topení: |  |  |  |  | Chlazení:
| Voda na přívodu |  |  | Voda na přívodu |  |  |  | 0
| Voda na zpátečce |  | 0 | Voda na zpátečce |  |  |  | 0
| "Suchá" teplota vzduchu |  | 0 | "Suchá" teplota vzduchu |  |  |  | 0
|  | Topení: // |  | Chlazení: // |  | Objem vody | Elektrický výkon [W] | Akustický tlak [dB(A)]**** | Akustický výkon [dB(A)]****
|  | Výkon Topení | Průtok vody | Výkon Chlazení | Průtok vody
Fans off (indicative value)
EN16430 | Rychlost otáček ventilátoru
Fan speed selection 2
Fan speed selection 3
Napětí ventilárotu [V]
* | Chladicí výkon vypočítán podle EN 16430 s ventilátory, které u všech typů - výšek foukají nahoru.
** | Když je objem vody uveden v galonech, jednotky jsou konkrétně imperiální galony.
*** | Akustický výkon podle ISO 3741: 2010, hladina akustického tlaku s předpokládaným útlumem místnosti o 8 dB (A).

## ExtraTaal1 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal2 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).

## ExtraTaal3 (hidden)
Selectiontool Strada Hybrid
| Length |  | mm | Formulary | Static device | rel. humid. | Unit | Copy all data
| Heigth |  | mm | Version | Hybrid device | Unit conversion | DBH set | SI-units
| Type |  |  | Temperatures | DBH rail type | Device |  | Imperial-units
| Depth |  | mm | If the fans are switched off, the output is an indicative value. | Water side pressure loss
| Heating: |  |  |  |  | Cooling:
| Supply water |  |  | Supply water |  |  |  | 0
| Return water |  | 0 | Return water |  |  |  | 0
| Entering air (dry bulb) |  | 0 | Entering air (dry bulb) |  |  |  | 0
|  | Heating: // |  | Cooling: // |  | Water volume | Electrical consumption [W] | Sound pressure level [dB(A)]**** | Sound power [dB(A)]****
|  | Heating capacity | Water flow | Cooling capacity | Water flow
Fans off (indicative value)
EN16430 | Fan speed
Fan speed selection 2
Fan speed selection 3
Fan voltage [V]
* | Cooling power is calcullated according EN16430 with fans blowing up for all heights.
** | When the water volume is given in gallons, the units are specifically imperial gallons.
*** | Soundpower according to ISO 3741:2010, sound pressure level with assumed room damping of 8 dB(A).